## modbus_addresses_all (2)
Title | Register type | Register | Division factor | Unit | Size of variable | Min value | Max value | Default value | Column1
Current outdoor temperature (BT1) | MODBUS_INPUT_REGISTER | 1 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP23-BT2) | MODBUS_INPUT_REGISTER | 2 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP22-BT2) | MODBUS_INPUT_REGISTER | 3 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP21-BT2) | MODBUS_INPUT_REGISTER | 4 | 10 | °C | s16 | 0 | 0 | 0
Collector in (AZ10-BT26) | MODBUS_INPUT_REGISTER | 21 | 10 | °C | s16 | 0 | 0 | 0
Collector out (AZ10-BT27) | MODBUS_INPUT_REGISTER | 22 | 10 | °C | s16 | 0 | 0 | 0
Return line (EQ1-BT65) | MODBUS_INPUT_REGISTER | 31 | 10 | °C | s16 | 0 | 0 | 0
Temperature limiter (EB100-FD1) | MODBUS_INPUT_REGISTER | 36 | 1 |  | s16 | 0 | 0 | 0
Average temperature (BT1) | MODBUS_INPUT_REGISTER | 37 | 10 | °C | s16 | 0 | 0 | 0
Boiler temperature (BT52) | MODBUS_INPUT_REGISTER | 38 | 10 | °C | s16 | 0 | 0 | 0
External supply line (BT25) | MODBUS_INPUT_REGISTER | 39 | 10 | °C | s16 | 0 | 0 | 0
Electrical anode (EB100-FR1) | MODBUS_INPUT_REGISTER | 41 | 1 |  | s16 | 0 | 0 | 0
Pool (CL12-BT51) | MODBUS_INPUT_REGISTER | 59 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 60 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 61 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 62 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 63 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 64 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 65 | 10 | °C | s16 | 0 | 0 | 0
Collector in (AZ13-BT26) | MODBUS_INPUT_REGISTER | 66 | 10 | °C | s16 | 0 | 0 | 0
Collector in (AZ12-BT26) | MODBUS_INPUT_REGISTER | 67 | 10 | °C | s16 | 0 | 0 | 0
Collector in (AZ11-BT26) | MODBUS_INPUT_REGISTER | 68 | 10 | °C | s16 | 0 | 0 | 0
Collector out (AZ13-BT27) | MODBUS_INPUT_REGISTER | 69 | 10 | °C | s16 | 0 | 0 | 0
Collector out (AZ12-BT27) | MODBUS_INPUT_REGISTER | 70 | 10 | °C | s16 | 0 | 0 | 0
Collector out (AZ11-BT27) | MODBUS_INPUT_REGISTER | 71 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP23-BT3) | MODBUS_INPUT_REGISTER | 75 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP22-BT3) | MODBUS_INPUT_REGISTER | 76 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP21-BT3) | MODBUS_INPUT_REGISTER | 77 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP15-BT3) | MODBUS_INPUT_REGISTER | 78 | 10 | °C | s16 | 0 | 0 | 0
Outgoing hot water (BT70) | MODBUS_INPUT_REGISTER | 87 | 10 | °C | s16 | 0 | 0 | 0
Return line (BT71) | MODBUS_INPUT_REGISTER | 88 | 10 | °C | s16 | 0 | 0 | 0
Collector (EQ1-BT57) | MODBUS_INPUT_REGISTER | 90 | 10 | °C | s16 | 0 | 0 | 0
Heating dump (EQ1-BT75) | MODBUS_INPUT_REGISTER | 91 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP47-BT2) | MODBUS_INPUT_REGISTER | 94 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP46-BT2) | MODBUS_INPUT_REGISTER | 95 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP45-BT2) | MODBUS_INPUT_REGISTER | 96 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP44-BT2) | MODBUS_INPUT_REGISTER | 97 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP47-BT3) | MODBUS_INPUT_REGISTER | 98 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP46-BT3) | MODBUS_INPUT_REGISTER | 99 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP45-BT3) | MODBUS_INPUT_REGISTER | 100 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP44-BT3) | MODBUS_INPUT_REGISTER | 101 | 10 | °C | s16 | 0 | 0 | 0
id:149 | MODBUS_INPUT_REGISTER | 108 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 8 (BT50) | MODBUS_INPUT_REGISTER | 109 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 7 (BT50) | MODBUS_INPUT_REGISTER | 110 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 6 (BT50) | MODBUS_INPUT_REGISTER | 111 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 5 (BT50) | MODBUS_INPUT_REGISTER | 112 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 4 (BT50) | MODBUS_INPUT_REGISTER | 113 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 3 (BT50) | MODBUS_INPUT_REGISTER | 114 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 2 (BT50) | MODBUS_INPUT_REGISTER | 115 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 1 (BT50) | MODBUS_INPUT_REGISTER | 116 | 10 | °C | s16 | 0 | 0 | 0
id:193 | MODBUS_INPUT_REGISTER | 128 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 8 | MODBUS_INPUT_REGISTER | 129 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 7 | MODBUS_INPUT_REGISTER | 130 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 6 | MODBUS_INPUT_REGISTER | 131 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 5 | MODBUS_INPUT_REGISTER | 132 | 1 |  | u8 | 0 | 0 | 0
id:246 | MODBUS_INPUT_REGISTER | 133 | 1 |  | u8 | 0 | 0 | 0
Relay status (ERS 1) | MODBUS_INPUT_REGISTER | 134 | 1 |  | u8 | 0 | 0 | 0
Fan speed (AZ30-GQ2) | MODBUS_INPUT_REGISTER | 135 | 1 | % | u8 | 0 | 0 | 0
Fan speed (AZ30-GQ3) | MODBUS_INPUT_REGISTER | 136 | 1 | % | u8 | 0 | 0 | 0
Current hot water mode controlled by | MODBUS_INPUT_REGISTER | 137 | 1 |  | s8 | 0 | 0 | 0
Max. compressor frequency, heating | MODBUS_INPUT_REGISTER | 141 | 100 | Hz | u16 | 0 | 0 | 0
External adjustment climate system 8 | MODBUS_INPUT_REGISTER | 151 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 7 | MODBUS_INPUT_REGISTER | 152 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 6 | MODBUS_INPUT_REGISTER | 153 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 5 | MODBUS_INPUT_REGISTER | 154 | 1 |  | u8 | 0 | 0 | 0
Climate system 8 | MODBUS_INPUT_REGISTER | 156 | 1 |  | u8 | 0 | 0 | 0
Climate system 7 | MODBUS_INPUT_REGISTER | 157 | 1 |  | u8 | 0 | 0 | 0
Climate system 6 | MODBUS_INPUT_REGISTER | 158 | 1 |  | u8 | 0 | 0 | 0
Climate system 5 | MODBUS_INPUT_REGISTER | 159 | 1 |  | u8 | 0 | 0 | 0
Extra cooling | MODBUS_INPUT_REGISTER | 160 | 1 |  | u8 | 0 | 0 | 0
Hot water comfort return (BT82) | MODBUS_INPUT_REGISTER | 174 | 10 | °C | s16 | 0 | 0 | 0
Hot water comfort heater (BT83) | MODBUS_INPUT_REGISTER | 175 | 10 | °C | s16 | 0 | 0 | 0
Compressor, total time pool, heat pump 8 (EP15) | MODBUS_INPUT_REGISTER | 179 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 8 (EP15) | MODBUS_INPUT_REGISTER | 181 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 8 (EP14) | MODBUS_INPUT_REGISTER | 185 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 8 (EP14) | MODBUS_INPUT_REGISTER | 187 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 7 (EP15) | MODBUS_INPUT_REGISTER | 191 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 7 (EP15) | MODBUS_INPUT_REGISTER | 193 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 7 (EP14) | MODBUS_INPUT_REGISTER | 197 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 7 (EP14) | MODBUS_INPUT_REGISTER | 199 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 6 (EP15) | MODBUS_INPUT_REGISTER | 203 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 6 (EP15) | MODBUS_INPUT_REGISTER | 205 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 6 (EP14) | MODBUS_INPUT_REGISTER | 209 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 6 (EP14) | MODBUS_INPUT_REGISTER | 211 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 5 (EP15) | MODBUS_INPUT_REGISTER | 215 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 5 (EP15) | MODBUS_INPUT_REGISTER | 217 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 5 (EP14) | MODBUS_INPUT_REGISTER | 221 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 5 (EP14) | MODBUS_INPUT_REGISTER | 223 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 4 (EP15) | MODBUS_INPUT_REGISTER | 227 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 4 (EP15) | MODBUS_INPUT_REGISTER | 229 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 4 (EP14) | MODBUS_INPUT_REGISTER | 233 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 4 (EP14) | MODBUS_INPUT_REGISTER | 235 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 3 (EP15) | MODBUS_INPUT_REGISTER | 239 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 3 (EP15) | MODBUS_INPUT_REGISTER | 241 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 3 (EP14) | MODBUS_INPUT_REGISTER | 245 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 3 (EP14) | MODBUS_INPUT_REGISTER | 247 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 2 (EP15) | MODBUS_INPUT_REGISTER | 251 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 2 (EP15) | MODBUS_INPUT_REGISTER | 253 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 2 (EP14) | MODBUS_INPUT_REGISTER | 257 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 2 (EP14) | MODBUS_INPUT_REGISTER | 259 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 1 (EP15) | MODBUS_INPUT_REGISTER | 263 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 1 (EP15) | MODBUS_INPUT_REGISTER | 265 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 1 (EP14) | MODBUS_INPUT_REGISTER | 269 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 1 (EP14) | MODBUS_INPUT_REGISTER | 271 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time cooling, main unit (EP14) | MODBUS_INPUT_REGISTER | 279 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, main unit (EP14) | MODBUS_INPUT_REGISTER | 281 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, main unit (EP14) | MODBUS_INPUT_REGISTER | 283 | 1 | h | u32 | 0 | 2147483647 | 0
Heat pump 8 requested compressor frequency | MODBUS_INPUT_REGISTER | 294 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 7 requested compressor frequency | MODBUS_INPUT_REGISTER | 295 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 6 requested compressor frequency | MODBUS_INPUT_REGISTER | 296 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 5 requested compressor frequency | MODBUS_INPUT_REGISTER | 297 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 4 requested compressor frequency | MODBUS_INPUT_REGISTER | 298 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 3 requested compressor frequency | MODBUS_INPUT_REGISTER | 299 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 2 requested compressor frequency | MODBUS_INPUT_REGISTER | 300 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 1 requested compressor frequency | MODBUS_INPUT_REGISTER | 301 | 1 | Hz | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 8 | MODBUS_INPUT_REGISTER | 303 | 1 |  | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 7 | MODBUS_INPUT_REGISTER | 304 | 1 |  | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 6 | MODBUS_INPUT_REGISTER | 305 | 1 |  | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 5 | MODBUS_INPUT_REGISTER | 306 | 1 |  | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 4 | MODBUS_INPUT_REGISTER | 307 | 1 |  | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 3 | MODBUS_INPUT_REGISTER | 308 | 1 |  | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 2 | MODBUS_INPUT_REGISTER | 309 | 1 |  | u8 | 0 | 0 | 0
Status (OPT) | MODBUS_INPUT_REGISTER | 311 | 1 |  | u8 | 0 | 0 | 0
Version (OPT) | MODBUS_INPUT_REGISTER | 312 | 1 |  | u16 | 0 | 0 | 0
OPT relay, modulation level | MODBUS_INPUT_REGISTER | 313 | 10 | % | s16 | 0 | 0 | 0
OPT operating time | MODBUS_INPUT_REGISTER | 315 | 1 | h | u16 | 0 | 0 | 0
Available compressors heating | MODBUS_INPUT_REGISTER | 317 | 1 |  | u8 | 0 | 0 | 0
Available compressors hot water | MODBUS_INPUT_REGISTER | 318 | 1 |  | u8 | 0 | 0 | 0
Available compressors pool 1 | MODBUS_INPUT_REGISTER | 319 | 1 |  | u8 | 0 | 0 | 0
Available compressors pool 2 | MODBUS_INPUT_REGISTER | 320 | 1 |  | u8 | 0 | 0 | 0
Available compressors cooling | MODBUS_INPUT_REGISTER | 321 | 1 |  | u8 | 0 | 0 | 0
Supply temperature (BT64) | MODBUS_INPUT_REGISTER | 337 | 10 | °C | s16 | 0 | 0 | 0
Heat pump functionality 2 | MODBUS_INPUT_REGISTER | 338 | 1 |  | u32 | 0 | 0 | 0
Status (S135) | MODBUS_INPUT_REGISTER | 344 | 1 |  | u8 | 0 | 0 | 0
Status, demand, pump speed (S135) | MODBUS_INPUT_REGISTER | 345 | 1 |  | u8 | 0 | 0 | 0
Status, demand, fan speed (S135) | MODBUS_INPUT_REGISTER | 346 | 1 |  | u8 | 0 | 0 | 0
Status, solenoid (S135) | MODBUS_INPUT_REGISTER | 347 | 1 |  | u8 | 0 | 0 | 0
Status, compressor, heater(S135) | MODBUS_INPUT_REGISTER | 348 | 1 |  | u8 | 0 | 0 | 0
Status, compressor, demand (S135) | MODBUS_INPUT_REGISTER | 350 | 1 |  | u8 | 0 | 0 | 0
Degree minutes | MODBUS_HOLDING_REGISTER | 11 | 10 | DM | s32 | -30000 | 30000 | 0
Blocking (ERS 1) | MODBUS_INPUT_REGISTER | 358 | 1 |  | u8 | 0 | 0 | 0
AZ30-EB17 | MODBUS_INPUT_REGISTER | 359 | 1 |  | u8 | 0 | 0 | 0
Supply line (S135-BT12) | MODBUS_INPUT_REGISTER | 360 | 10 | °C | s16 | 0 | 0 | 0
Return line (S135-BT13) | MODBUS_INPUT_REGISTER | 361 | 10 | °C | s16 | 0 | 0 | 0
Evaporator (S135-BT16) | MODBUS_INPUT_REGISTER | 362 | 10 | °C | s16 | 0 | 0 | 0
Defrosting sensor (S135-BT76) | MODBUS_INPUT_REGISTER | 363 | 10 | °C | s16 | 0 | 0 | 0
Incoming air (S135-BT77) | MODBUS_INPUT_REGISTER | 364 | 10 | °C | s16 | 0 | 0 | 0
Alarm number (S135) | MODBUS_INPUT_REGISTER | 365 | 1 |  | u16 | 0 | 0 | 0
Defrosting (S135) | MODBUS_INPUT_REGISTER | 366 | 1 |  | u8 | 0 | 0 | 0
Status, relay 5 (S135) | MODBUS_INPUT_REGISTER | 367 | 1 |  | u8 | 0 | 0 | 0
Status, relay 4 (S135) | MODBUS_INPUT_REGISTER | 368 | 1 |  | u8 | 0 | 0 | 0
Status, relay 3 (S135) | MODBUS_INPUT_REGISTER | 369 | 1 |  | u8 | 0 | 0 | 0
Status, relay 2 (S135) | MODBUS_INPUT_REGISTER | 370 | 1 |  | u8 | 0 | 0 | 0
Status, relay 1 (S135) | MODBUS_INPUT_REGISTER | 371 | 1 |  | u8 | 0 | 0 | 0
Status, relay 0 (S135) | MODBUS_INPUT_REGISTER | 372 | 1 |  | u8 | 0 | 0 | 0
Pump speed (S135) | MODBUS_INPUT_REGISTER | 373 | 1 | % | u8 | 0 | 0 | 0
Selected fan speed | MODBUS_INPUT_REGISTER | 374 | 1 | % | u8 | 0 | 0 | 0
Version (S135) | MODBUS_INPUT_REGISTER | 376 | 1 |  | u16 | 0 | 0 | 0
id:803 | MODBUS_INPUT_REGISTER | 377 | 1 |  | u32 | 0 | 2147483647 | 0
id:804 | MODBUS_INPUT_REGISTER | 379 | 1 |  | u32 | 0 | 0 | 0
id:805 | MODBUS_INPUT_REGISTER | 381 | 1 |  | u32 | 0 | 2147483647 | 0
id:806 | MODBUS_INPUT_REGISTER | 383 | 1 |  | u32 | 0 | 0 | 0
Seconds of blank time left, charge pump 8 | MODBUS_INPUT_REGISTER | 385 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 7 | MODBUS_INPUT_REGISTER | 386 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 6 | MODBUS_INPUT_REGISTER | 387 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 5 | MODBUS_INPUT_REGISTER | 388 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 4 | MODBUS_INPUT_REGISTER | 389 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 3 | MODBUS_INPUT_REGISTER | 390 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 2 | MODBUS_INPUT_REGISTER | 391 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 1 | MODBUS_INPUT_REGISTER | 392 | 1 |  | u8 | 0 | 0 | 0
Alarm number from outdoor air heat pump (EB101) | MODBUS_INPUT_REGISTER | 400 | 1 |  | u8 | 0 | 0 | 0
Fan speed (EB101) | MODBUS_INPUT_REGISTER | 401 | 1 | rpm | u16 | 0 | 0 | 0
Max fan speed (EB101) | MODBUS_INPUT_REGISTER | 402 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB101) | MODBUS_INPUT_REGISTER | 403 | 1 | rpm | u16 | 0 | 0 | 0
Max compressor speed (EB101) | MODBUS_INPUT_REGISTER | 404 | 10 | Hz | u16 | 0 | 0 | 0
Min compressor speed (EB101) | MODBUS_INPUT_REGISTER | 405 | 10 | Hz | u16 | 0 | 0 | 0
Generated power heating (EB101) | MODBUS_INPUT_REGISTER | 406 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB101) | MODBUS_INPUT_REGISTER | 407 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB101) | MODBUS_INPUT_REGISTER | 408 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB101) | MODBUS_INPUT_REGISTER | 409 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB101) | MODBUS_INPUT_REGISTER | 410 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB101) | MODBUS_INPUT_REGISTER | 411 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB101) | MODBUS_INPUT_REGISTER | 412 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB101) | MODBUS_INPUT_REGISTER | 413 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB101) | MODBUS_INPUT_REGISTER | 414 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB101) | MODBUS_INPUT_REGISTER | 415 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB101) | MODBUS_INPUT_REGISTER | 416 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB101) | MODBUS_INPUT_REGISTER | 417 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB101) | MODBUS_INPUT_REGISTER | 418 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB101) | MODBUS_INPUT_REGISTER | 419 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB101) | MODBUS_INPUT_REGISTER | 420 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB101) | MODBUS_INPUT_REGISTER | 421 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB101) | MODBUS_INPUT_REGISTER | 422 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open in (EVI)(EB101) | MODBUS_INPUT_REGISTER | 423 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB101) | MODBUS_INPUT_REGISTER | 424 | 1 |  | u16 | 0 | 0 | 0
id:859 | MODBUS_INPUT_REGISTER | 426 | 10 | %RH | s16 | 0 | 0 | 0
id:861 | MODBUS_INPUT_REGISTER | 427 | 1 |  | u32 | 0 | 0 | 0
id:862 | MODBUS_INPUT_REGISTER | 429 | 1 |  | u16 | 0 | 0 | 0
Low press (EB108 BP8 dew) | MODBUS_INPUT_REGISTER | 438 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB108 BP9 dew) | MODBUS_INPUT_REGISTER | 439 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB108-BP11) | MODBUS_INPUT_REGISTER | 441 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB108-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 442 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB108-EP14) | MODBUS_INPUT_REGISTER | 444 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB108-EP14) | MODBUS_INPUT_REGISTER | 445 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB107 BP8 dew) | MODBUS_INPUT_REGISTER | 454 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB107 BP9 dew) | MODBUS_INPUT_REGISTER | 455 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB107-BP11) | MODBUS_INPUT_REGISTER | 457 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB107-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 458 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB107-EP14) | MODBUS_INPUT_REGISTER | 460 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB107-EP14) | MODBUS_INPUT_REGISTER | 461 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB106 BP8 dew) | MODBUS_INPUT_REGISTER | 470 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB106 BP9 dew) | MODBUS_INPUT_REGISTER | 471 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB106-BP11) | MODBUS_INPUT_REGISTER | 473 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB106-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 474 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB106-EP14) | MODBUS_INPUT_REGISTER | 476 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB106-EP14) | MODBUS_INPUT_REGISTER | 477 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB105 BP8 dew) | MODBUS_INPUT_REGISTER | 486 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB105 BP9 dew) | MODBUS_INPUT_REGISTER | 487 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB105-BP11) | MODBUS_INPUT_REGISTER | 489 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB105-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 490 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB105-EP14) | MODBUS_INPUT_REGISTER | 492 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB105-EP14) | MODBUS_INPUT_REGISTER | 493 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB104 BP8 dew) | MODBUS_INPUT_REGISTER | 502 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB104 BP9 dew) | MODBUS_INPUT_REGISTER | 503 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB104-BP11) | MODBUS_INPUT_REGISTER | 505 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB104-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 506 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB104-EP14) | MODBUS_INPUT_REGISTER | 508 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB104-EP14) | MODBUS_INPUT_REGISTER | 509 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB103 BP8 dew) | MODBUS_INPUT_REGISTER | 518 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB103 BP9 dew) | MODBUS_INPUT_REGISTER | 519 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB103-BP11) | MODBUS_INPUT_REGISTER | 521 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB103-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 522 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB103-EP14) | MODBUS_INPUT_REGISTER | 524 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB103-EP14) | MODBUS_INPUT_REGISTER | 525 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB102 BP8 dew) | MODBUS_INPUT_REGISTER | 534 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB102 BP9 dew) | MODBUS_INPUT_REGISTER | 535 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB102-EP14-BP11) | MODBUS_INPUT_REGISTER | 537 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB102-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 538 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB102-EP14) | MODBUS_INPUT_REGISTER | 540 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB102-EP14) | MODBUS_INPUT_REGISTER | 541 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB101 BP8 dew) | MODBUS_INPUT_REGISTER | 550 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB101 BP9 dew) | MODBUS_INPUT_REGISTER | 551 | 10 | °C | s16 | 0 | 0 | 0
Injection (EB101-BT81) | MODBUS_INPUT_REGISTER | 552 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB101-BP11) | MODBUS_INPUT_REGISTER | 553 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB101-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 554 | 10 | °C | s16 | 0 | 0 | 0
Evaporator (EB101-BT84) | MODBUS_INPUT_REGISTER | 555 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB101-EP14) | MODBUS_INPUT_REGISTER | 556 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB101-EP14) | MODBUS_INPUT_REGISTER | 557 | 1 | rpm | u16 | 0 | 0 | 0
High condenser out alarm (S135) | MODBUS_INPUT_REGISTER | 575 | 1 |  | u16 | 0 | 0 | 0
High condenser in alarm (S135) | MODBUS_INPUT_REGISTER | 576 | 1 |  | u16 | 0 | 0 | 0
Operating mode PV panels | MODBUS_INPUT_REGISTER | 579 | 1 |  | u8 | 0 | 0 | 0
EME lux mode without EME | MODBUS_INPUT_REGISTER | 581 | 1 |  | u8 | 0 | 0 | 0
Timer (EME) | MODBUS_INPUT_REGISTER | 582 | 60 | min | u16 | 0 | 0 | 0
Fan mode 4 | MODBUS_INPUT_REGISTER | 590 | 1 | % | u8 | 0 | 0 | 0
Fan mode 3 | MODBUS_INPUT_REGISTER | 591 | 1 | % | u8 | 0 | 0 | 0
Fan mode 2 | MODBUS_INPUT_REGISTER | 592 | 1 | % | u8 | 0 | 0 | 0
Is the compressor accessible | MODBUS_INPUT_REGISTER | 593 | 1 |  | u8 | 0 | 0 | 0
Prio, hot water (OPT) | MODBUS_INPUT_REGISTER | 604 | 1 |  | u8 | 0 | 0 | 0
Permit (undefined) | MODBUS_INPUT_REGISTER | 683 | 1 |  | u8 | 0 | 0 | 0
Permit (undefined) | MODBUS_INPUT_REGISTER | 684 | 1 |  | u8 | 0 | 0 | 0
Permit (undefined) | MODBUS_INPUT_REGISTER | 685 | 1 |  | u8 | 0 | 0 | 0
Permit (OPT 10) additional heat | MODBUS_INPUT_REGISTER | 686 | 1 |  | u8 | 0 | 0 | 0
Permit ext. imm. heater step | MODBUS_INPUT_REGISTER | 687 | 1 |  | u8 | 0 | 0 | 0
Permit int. imm. heater step | MODBUS_INPUT_REGISTER | 688 | 1 |  | u8 | 0 | 0 | 0
Permit shunted additional heat | MODBUS_INPUT_REGISTER | 689 | 1 |  | u8 | 0 | 0 | 0
Permit prioritised additional heat | MODBUS_INPUT_REGISTER | 690 | 1 |  | u8 | 0 | 0 | 0
Permit (EB108-EP15) | MODBUS_INPUT_REGISTER | 691 | 1 |  | u8 | 0 | 0 | 0
Permit (EB107-EP15) | MODBUS_INPUT_REGISTER | 692 | 1 |  | u8 | 0 | 0 | 0
Permit (EB106-EP15) | MODBUS_INPUT_REGISTER | 693 | 1 |  | u8 | 0 | 0 | 0
Permit (EB105-EP15) | MODBUS_INPUT_REGISTER | 694 | 1 |  | u8 | 0 | 0 | 0
Permit (EB104-EP15) | MODBUS_INPUT_REGISTER | 695 | 1 |  | u8 | 0 | 0 | 0
Permit (EB103-EP15) | MODBUS_INPUT_REGISTER | 696 | 1 |  | u8 | 0 | 0 | 0
Permit (EB102-EP15) | MODBUS_INPUT_REGISTER | 697 | 1 |  | u8 | 0 | 0 | 0
Permit (EB101-EP15) | MODBUS_INPUT_REGISTER | 698 | 1 |  | u8 | 0 | 0 | 0
Permit (EB100-EP15) | MODBUS_INPUT_REGISTER | 699 | 1 |  | u8 | 0 | 0 | 0
Permit (EB108-EP14) | MODBUS_INPUT_REGISTER | 700 | 1 |  | u8 | 0 | 0 | 0
Permit (EB107-EP14) | MODBUS_INPUT_REGISTER | 701 | 1 |  | u8 | 0 | 0 | 0
Permit (EB106-EP14) | MODBUS_INPUT_REGISTER | 702 | 1 |  | u8 | 0 | 0 | 0
Permit (EB105-EP14) | MODBUS_INPUT_REGISTER | 703 | 1 |  | u8 | 0 | 0 | 0
Permit (EB104-EP14) | MODBUS_INPUT_REGISTER | 704 | 1 |  | u8 | 0 | 0 | 0
Permit (EB103-EP14) | MODBUS_INPUT_REGISTER | 705 | 1 |  | u8 | 0 | 0 | 0
Permit (EB102-EP14) | MODBUS_INPUT_REGISTER | 706 | 1 |  | u8 | 0 | 0 | 0
Permit (EB101-EP14) | MODBUS_INPUT_REGISTER | 707 | 1 |  | u8 | 0 | 0 | 0
Permit (EB100-EP14) | MODBUS_INPUT_REGISTER | 708 | 1 |  | u8 | 0 | 0 | 0
Smart energy source, priority 7, start DM | MODBUS_INPUT_REGISTER | 709 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 6, start DM | MODBUS_INPUT_REGISTER | 711 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 5, start DM | MODBUS_INPUT_REGISTER | 713 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 4, start DM | MODBUS_INPUT_REGISTER | 715 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 3, start DM | MODBUS_INPUT_REGISTER | 717 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 2, start DM | MODBUS_INPUT_REGISTER | 719 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 1, start DM | MODBUS_INPUT_REGISTER | 721 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 7, stop DM | MODBUS_INPUT_REGISTER | 723 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 6, stop DM | MODBUS_INPUT_REGISTER | 725 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 5, stop DM | MODBUS_INPUT_REGISTER | 727 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 4, stop DM | MODBUS_INPUT_REGISTER | 729 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 3, stop DM | MODBUS_INPUT_REGISTER | 731 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 2, stop DM | MODBUS_INPUT_REGISTER | 733 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 1, stop DM | MODBUS_INPUT_REGISTER | 735 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, DM minimum value | MODBUS_INPUT_REGISTER | 737 | 1 |  | s32 | 0 | 0 | 0
External guide status | MODBUS_INPUT_REGISTER | 745 | 1 |  | u8 | 0 | 0 | 0
Test guide value | MODBUS_INPUT_REGISTER | 746 | 1 |  | u16 | 0 | 0 | 0
Temp. lux forces start of hot water demand | MODBUS_INPUT_REGISTER | 747 | 1 |  | u8 | 0 | 0 | 0
Smart energy source, prio OPT10 for hot water | MODBUS_INPUT_REGISTER | 757 | 1 |  | u8 | 0 | 0 | 0
Wood boiler activated | MODBUS_INPUT_REGISTER | 759 | 1 |  | u8 | 0 | 0 | 0
Max fan speed (EB108-F21x0) | MODBUS_INPUT_REGISTER | 762 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB108) | MODBUS_INPUT_REGISTER | 763 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB108) | MODBUS_INPUT_REGISTER | 766 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB108) | MODBUS_INPUT_REGISTER | 767 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB108) | MODBUS_INPUT_REGISTER | 768 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB108) | MODBUS_INPUT_REGISTER | 769 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB108) | MODBUS_INPUT_REGISTER | 770 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB108) | MODBUS_INPUT_REGISTER | 771 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB108) | MODBUS_INPUT_REGISTER | 772 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB108) | MODBUS_INPUT_REGISTER | 773 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB108) | MODBUS_INPUT_REGISTER | 774 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB108) | MODBUS_INPUT_REGISTER | 775 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB108) | MODBUS_INPUT_REGISTER | 776 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB108) | MODBUS_INPUT_REGISTER | 777 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB108) | MODBUS_INPUT_REGISTER | 778 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB108) | MODBUS_INPUT_REGISTER | 779 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB108) | MODBUS_INPUT_REGISTER | 780 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB108) | MODBUS_INPUT_REGISTER | 781 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB108) | MODBUS_INPUT_REGISTER | 782 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB108) | MODBUS_INPUT_REGISTER | 783 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB108) | MODBUS_INPUT_REGISTER | 784 | 1 |  | u16 | 0 | 0 | 0
Max fan speed (EB107) | MODBUS_INPUT_REGISTER | 787 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB107) | MODBUS_INPUT_REGISTER | 788 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB107) | MODBUS_INPUT_REGISTER | 791 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB107) | MODBUS_INPUT_REGISTER | 792 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB107) | MODBUS_INPUT_REGISTER | 793 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB107) | MODBUS_INPUT_REGISTER | 794 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB107) | MODBUS_INPUT_REGISTER | 795 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB107) | MODBUS_INPUT_REGISTER | 796 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB107) | MODBUS_INPUT_REGISTER | 797 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB107) | MODBUS_INPUT_REGISTER | 798 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB107) | MODBUS_INPUT_REGISTER | 799 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB107) | MODBUS_INPUT_REGISTER | 800 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB107) | MODBUS_INPUT_REGISTER | 801 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB107) | MODBUS_INPUT_REGISTER | 802 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB107) | MODBUS_INPUT_REGISTER | 803 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB107) | MODBUS_INPUT_REGISTER | 804 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB107) | MODBUS_INPUT_REGISTER | 805 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB107) | MODBUS_INPUT_REGISTER | 806 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB107) | MODBUS_INPUT_REGISTER | 807 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB107) | MODBUS_INPUT_REGISTER | 808 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB107) | MODBUS_INPUT_REGISTER | 809 | 1 |  | u16 | 0 | 0 | 0
Max fan speed (EB106) | MODBUS_INPUT_REGISTER | 812 | 1 | rpm | u16 | 0 | 0 | 0
id:1309 | MODBUS_INPUT_REGISTER | 813 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB106) | MODBUS_INPUT_REGISTER | 816 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB106) | MODBUS_INPUT_REGISTER | 817 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB106) | MODBUS_INPUT_REGISTER | 818 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB106) | MODBUS_INPUT_REGISTER | 819 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB106) | MODBUS_INPUT_REGISTER | 820 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB106) | MODBUS_INPUT_REGISTER | 821 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB106) | MODBUS_INPUT_REGISTER | 822 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB106) | MODBUS_INPUT_REGISTER | 823 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB106) | MODBUS_INPUT_REGISTER | 824 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB106) | MODBUS_INPUT_REGISTER | 825 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB106) | MODBUS_INPUT_REGISTER | 826 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB106) | MODBUS_INPUT_REGISTER | 827 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB106) | MODBUS_INPUT_REGISTER | 828 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB106) | MODBUS_INPUT_REGISTER | 829 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB106) | MODBUS_INPUT_REGISTER | 830 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB106) | MODBUS_INPUT_REGISTER | 831 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB106) | MODBUS_INPUT_REGISTER | 832 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB106) | MODBUS_INPUT_REGISTER | 833 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB106) | MODBUS_INPUT_REGISTER | 834 | 1 |  | u16 | 0 | 0 | 0
Max fan speed (EB105) | MODBUS_INPUT_REGISTER | 837 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB105) | MODBUS_INPUT_REGISTER | 838 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB105) | MODBUS_INPUT_REGISTER | 841 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB105) | MODBUS_INPUT_REGISTER | 842 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB105) | MODBUS_INPUT_REGISTER | 843 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB105) | MODBUS_INPUT_REGISTER | 844 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB105) | MODBUS_INPUT_REGISTER | 845 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB105) | MODBUS_INPUT_REGISTER | 846 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB105) | MODBUS_INPUT_REGISTER | 847 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB105) | MODBUS_INPUT_REGISTER | 848 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB105) | MODBUS_INPUT_REGISTER | 849 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB105) | MODBUS_INPUT_REGISTER | 850 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB105) | MODBUS_INPUT_REGISTER | 851 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB105) | MODBUS_INPUT_REGISTER | 852 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB105) | MODBUS_INPUT_REGISTER | 853 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB105) | MODBUS_INPUT_REGISTER | 854 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB105) | MODBUS_INPUT_REGISTER | 855 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB105) | MODBUS_INPUT_REGISTER | 856 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB105) | MODBUS_INPUT_REGISTER | 857 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB105) | MODBUS_INPUT_REGISTER | 858 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB105) | MODBUS_INPUT_REGISTER | 859 | 1 |  | u16 | 0 | 0 | 0
Max fan speed (EB104) | MODBUS_INPUT_REGISTER | 862 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB104) | MODBUS_INPUT_REGISTER | 863 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB104) | MODBUS_INPUT_REGISTER | 866 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB104) | MODBUS_INPUT_REGISTER | 867 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB104) | MODBUS_INPUT_REGISTER | 868 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB104) | MODBUS_INPUT_REGISTER | 869 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB104) | MODBUS_INPUT_REGISTER | 870 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB104) | MODBUS_INPUT_REGISTER | 871 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB104) | MODBUS_INPUT_REGISTER | 872 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB104) | MODBUS_INPUT_REGISTER | 873 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB104) | MODBUS_INPUT_REGISTER | 874 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB104) | MODBUS_INPUT_REGISTER | 875 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB104) | MODBUS_INPUT_REGISTER | 876 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB104) | MODBUS_INPUT_REGISTER | 877 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB104) | MODBUS_INPUT_REGISTER | 878 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB104) | MODBUS_INPUT_REGISTER | 879 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB104) | MODBUS_INPUT_REGISTER | 880 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB104) | MODBUS_INPUT_REGISTER | 881 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB104) | MODBUS_INPUT_REGISTER | 882 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB104) | MODBUS_INPUT_REGISTER | 883 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB104) | MODBUS_INPUT_REGISTER | 884 | 1 |  | u16 | 0 | 0 | 0
Max fan speed (EB103) | MODBUS_INPUT_REGISTER | 887 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB103) | MODBUS_INPUT_REGISTER | 888 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB103) | MODBUS_INPUT_REGISTER | 891 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB103) | MODBUS_INPUT_REGISTER | 892 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB103) | MODBUS_INPUT_REGISTER | 893 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB103) | MODBUS_INPUT_REGISTER | 894 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB103) | MODBUS_INPUT_REGISTER | 895 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB103) | MODBUS_INPUT_REGISTER | 896 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB103) | MODBUS_INPUT_REGISTER | 897 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB103) | MODBUS_INPUT_REGISTER | 898 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB103) | MODBUS_INPUT_REGISTER | 899 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB103) | MODBUS_INPUT_REGISTER | 900 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB103) | MODBUS_INPUT_REGISTER | 901 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB103) | MODBUS_INPUT_REGISTER | 902 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB103) | MODBUS_INPUT_REGISTER | 903 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB103) | MODBUS_INPUT_REGISTER | 904 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB103) | MODBUS_INPUT_REGISTER | 905 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB103) | MODBUS_INPUT_REGISTER | 906 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB103) | MODBUS_INPUT_REGISTER | 907 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB103) | MODBUS_INPUT_REGISTER | 908 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB103) | MODBUS_INPUT_REGISTER | 909 | 1 |  | u16 | 0 | 0 | 0
Fan speed (EB102) | MODBUS_INPUT_REGISTER | 911 | 1 | rpm | u16 | 0 | 0 | 0
Max fan speed (EB102) | MODBUS_INPUT_REGISTER | 912 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB102) | MODBUS_INPUT_REGISTER | 913 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB102 | MODBUS_INPUT_REGISTER | 916 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB102) | MODBUS_INPUT_REGISTER | 917 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB102) | MODBUS_INPUT_REGISTER | 918 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB102) | MODBUS_INPUT_REGISTER | 919 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB102) | MODBUS_INPUT_REGISTER | 920 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB102) | MODBUS_INPUT_REGISTER | 921 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB101) | MODBUS_INPUT_REGISTER | 922 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB102) | MODBUS_INPUT_REGISTER | 923 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB102) | MODBUS_INPUT_REGISTER | 924 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB102) | MODBUS_INPUT_REGISTER | 925 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB102) | MODBUS_INPUT_REGISTER | 926 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB102) | MODBUS_INPUT_REGISTER | 927 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB102) | MODBUS_INPUT_REGISTER | 928 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB102) | MODBUS_INPUT_REGISTER | 929 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB102) | MODBUS_INPUT_REGISTER | 930 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB102) | MODBUS_INPUT_REGISTER | 931 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB102) | MODBUS_INPUT_REGISTER | 932 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB102) | MODBUS_INPUT_REGISTER | 933 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB102) | MODBUS_INPUT_REGISTER | 934 | 1 |  | u16 | 0 | 0 | 0
Smart energy source, priority select. in hot water | MODBUS_INPUT_REGISTER | 991 | 1 |  | u8 | 0 | 0 | 0
Outd. air heat pump, inverter, limits | MODBUS_INPUT_REGISTER | 992 | 1 |  | u8 | 0 | 0 | 0
Outd. air heat pump, inverter, speed reducing | MODBUS_INPUT_REGISTER | 993 | 1 |  | u8 | 0 | 0 | 0
Has one phase (EB101) | MODBUS_INPUT_REGISTER | 1008 | 1 |  | u8 | 0 | 0 | 0
Serial index (EB101) | MODBUS_INPUT_REGISTER | 1009 | 1 |  | u8 | 0 | 0 | 0
Limit DM | MODBUS_HOLDING_REGISTER | 18 | 10 | DM | s16 | -30000 | 30000 | 0
Calculated supply climate system 1 | MODBUS_INPUT_REGISTER | 1017 | 10 | °C | s16 | 0 | 0 | 0
Class 1 alarm | MODBUS_INPUT_REGISTER | 2195 | 1 |  | u8 | 0 | 0 | 0
Frost protection status | MODBUS_INPUT_REGISTER | 1018 | 1 |  | u16 | 0 | 0 | 0
Cooling status | MODBUS_INPUT_REGISTER | 1019 | 1 |  | u8 | 0 | 0 | 0
id:1726 | MODBUS_HOLDING_REGISTER | 2757 | 1 |  | s16 | 0 | 30000 | 0
Total run time additional heat | MODBUS_INPUT_REGISTER | 1025 | 10 | h | s32 | 0 | 1000000 | 0
Priority | MODBUS_INPUT_REGISTER | 1028 | 1 |  | u8 | 0 | 0 | 0
Operating mode internal add. heat | MODBUS_INPUT_REGISTER | 1029 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 4 | MODBUS_INPUT_REGISTER | 1030 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 3 | MODBUS_INPUT_REGISTER | 1031 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 2 | MODBUS_INPUT_REGISTER | 1032 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 1 | MODBUS_INPUT_REGISTER | 1033 | 1 |  | u8 | 0 | 0 | 0
Operating. mode shunt controlled additional heat | MODBUS_INPUT_REGISTER | 1034 | 1 |  | u8 | 0 | 0 | 0
Fan mode 1 | MODBUS_INPUT_REGISTER | 1037 | 1 | % | u8 | 0 | 0 | 0
Current hot water mode | MODBUS_INPUT_REGISTER | 1038 | 1 |  | s8 | 0 | 0 | 0
Blocking cooling | MODBUS_INPUT_REGISTER | 1053 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 4 | MODBUS_INPUT_REGISTER | 1054 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 3 | MODBUS_INPUT_REGISTER | 1055 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 2 | MODBUS_INPUT_REGISTER | 1056 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 1 | MODBUS_INPUT_REGISTER | 1057 | 1 |  | u8 | 0 | 0 | 0
External blocking | MODBUS_INPUT_REGISTER | 1058 | 1 |  | u8 | 0 | 0 | 0
Blocked | MODBUS_INPUT_REGISTER | 1059 | 1 |  | u8 | 0 | 0 | 0
External blocking, active cooling (HPAC) | MODBUS_INPUT_REGISTER | 1060 | 1 |  | u8 | 0 | 0 | 0
External blocking, passive cooling (HPAC) | MODBUS_INPUT_REGISTER | 1061 | 1 |  | u8 | 0 | 0 | 0
Step controlled add. heat blocking | MODBUS_INPUT_REGISTER | 1062 | 1 |  | u8 | 0 | 0 | 0
Hot water circulation (GP11) | MODBUS_INPUT_REGISTER | 1063 | 1 |  | u8 | 0 | 0 | 0
External heating medium pump (GP10) status | MODBUS_INPUT_REGISTER | 1066 | 1 |  | u8 | 0 | 0 | 0
Total HW run time additional heat | MODBUS_INPUT_REGISTER | 1069 | 10 | h | s32 | 0 | 9999999 | 0
More hot water status | MODBUS_INPUT_REGISTER | 1078 | 1 |  | u8 | 0 | 0 | 0
Relay status (HPAC) | MODBUS_INPUT_REGISTER | 1079 | 1 |  | u8 | 0 | 0 | 0
Holiday function status | MODBUS_HOLDING_REGISTER | 19 | 1 |  | s8 | 0 | 0 | 0
Docked compressors heating | MODBUS_INPUT_REGISTER | 1108 | 1 |  | u8 | 0 | 0 | 0
Docked compressors hot water | MODBUS_INPUT_REGISTER | 1109 | 1 |  | u8 | 0 | 0 | 0
Docked compressors pool 1 | MODBUS_INPUT_REGISTER | 1110 | 1 |  | u8 | 0 | 0 | 0
Reversing valve hot water (QN10) | MODBUS_INPUT_REGISTER | 2196 | 1 |  | u8 | 0 | 0 | 0
Relay status, base board (EB100-EP14) | MODBUS_INPUT_REGISTER | 1117 | 1 |  | u8 | 0 | 0 | 0
Relay status, imm. heat. board (EB100-EP14) | MODBUS_INPUT_REGISTER | 1119 | 1 |  | u16 | 0 | 0 | 0
Current status | MODBUS_INPUT_REGISTER | 1120 | 1 |  | u32 | 0 | 0 | 0
Functionality, heat pump (EP14) | MODBUS_INPUT_REGISTER | 1122 | 1 |  | u32 | 0 | 0 | 0
Active heat pumps | MODBUS_INPUT_REGISTER | 1124 | 1 |  | u16 | 0 | 0 | 0
Functionality, heat pump (EP15) | MODBUS_INPUT_REGISTER | 1125 | 1 |  | u32 | 0 | 0 | 0
Operating mode HW comfort | MODBUS_INPUT_REGISTER | 1129 | 1 |  | u8 | 0 | 0 | 0
Operating mode HW comfort additional heat | MODBUS_INPUT_REGISTER | 1130 | 1 |  | u8 | 0 | 0 | 0
Blocked | MODBUS_INPUT_REGISTER | 1131 | 1 |  | u8 | 0 | 0 | 0
Blocked | MODBUS_INPUT_REGISTER | 1132 | 1 |  | u8 | 0 | 0 | 0
Pool 2 (QN19) | MODBUS_INPUT_REGISTER | 1133 | 1 |  | u8 | 0 | 0 | 0
Pool 1 (QN19) | MODBUS_INPUT_REGISTER | 1134 | 1 |  | u8 | 0 | 0 | 0
Docked compressors pool 2 | MODBUS_INPUT_REGISTER | 1135 | 1 |  | u8 | 0 | 0 | 0
Version (EB101) | MODBUS_INPUT_REGISTER | 1451 | 1 |  | u16 | 0 | 0 | 0
Heat pump type (EB101) | MODBUS_INPUT_REGISTER | 1452 | 1 |  | u8 | 0 | 0 | 0
Compressor size (EB101) | MODBUS_INPUT_REGISTER | 1453 | 1 |  | u8 | 0 | 0 | 0
Return line (EB101-BT3) | MODBUS_INPUT_REGISTER | 1475 | 10 | °C | s16 | 0 | 0 | 0
Condenser sensor, supply line (EB101-BT12) | MODBUS_INPUT_REGISTER | 1478 | 10 | °C | s16 | 0 | 0 | 0
Discharge (EB101-BT14) | MODBUS_INPUT_REGISTER | 1479 | 10 | °C | s16 | 0 | 0 | 0
Liquid line (EB101-BT15) | MODBUS_INPUT_REGISTER | 1480 | 10 | °C | s16 | 0 | 0 | 0
Suction gas (EB101-BT17) | MODBUS_INPUT_REGISTER | 1481 | 10 | °C | s16 | 0 | 0 | 0
Compressor sensor (EB101-BT29) | MODBUS_INPUT_REGISTER | 1482 | 10 | °C | s16 | 0 | 0 | 0
Compressor status (EB101) | MODBUS_INPUT_REGISTER | 1484 | 1 |  | u8 | 0 | 0 | 0
Compressor, time to start (EB101-EP14) | MODBUS_INPUT_REGISTER | 1485 | 1 | min | u8 | 0 | 0 | 0
Relay status (EB101-EP14) | MODBUS_INPUT_REGISTER | 1486 | 1 |  | u16 | 0 | 0 | 0
Compressor, number of starts (EB101-EP14) | MODBUS_INPUT_REGISTER | 1489 | 1 |  | u32 | 0 | 2147483647 | 0
Compressor, oper. time, total (EB101-EP14) | MODBUS_INPUT_REGISTER | 1491 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, oper. time, hot water (EB101-EP14) | MODBUS_INPUT_REGISTER | 1493 | 1 | h | u32 | 0 | 2147483647 | 0
Alarm number (EB101-EP14) | MODBUS_INPUT_REGISTER | 1495 | 1 |  | u16 | 0 | 0 | 0
Version (EB100) | MODBUS_INPUT_REGISTER | 1496 | 1 |  | u16 | 0 | 0 | 0
Heat pump type (EB100) | MODBUS_INPUT_REGISTER | 1497 | 1 |  | u8 | 0 | 0 | 0
Compressor size (EB100) | MODBUS_INPUT_REGISTER | 1498 | 1 |  | u8 | 0 | 0 | 0
Compressor, oper. time, total (EB100-EP15) | MODBUS_INPUT_REGISTER | 1515 | 1 | h | u32 | 0 | 0 | 0
Compressor, oper. time, hot water (EB100-EP15) | MODBUS_INPUT_REGISTER | 1517 | 1 | h | u32 | 0 | 0 | 0
Return line (EB100-BT3) | MODBUS_INPUT_REGISTER | 1520 | 10 | °C | s16 | 0 | 0 | 0
Brine in (EB100-BT10) | MODBUS_INPUT_REGISTER | 1521 | 10 | °C | s16 | 0 | 0 | 0
Brine out (EB100-BT11) | MODBUS_INPUT_REGISTER | 1522 | 10 | °C | s16 | 0 | 0 | 0
Condenser (EB100-BT2) | MODBUS_INPUT_REGISTER | 1523 | 10 | °C | s16 | 0 | 0 | 0
Discharge (EB100-BT14) | MODBUS_INPUT_REGISTER | 1524 | 10 | °C | s16 | 0 | 0 | 0
Liquid line (EB100-BT15) | MODBUS_INPUT_REGISTER | 1525 | 10 | °C | s16 | 0 | 0 | 0
Suction gas (EB100-BT17) | MODBUS_INPUT_REGISTER | 1526 | 10 | °C | s16 | 0 | 0 | 0
Compressor sensor (EB100-BT29) | MODBUS_INPUT_REGISTER | 1527 | 10 | °C | s16 | 0 | 0 | 0
Low press (EB100-BP8) | MODBUS_INPUT_REGISTER | 1528 | 10 | °C | s16 | 0 | 0 | 0
Compressor status (EB100) | MODBUS_INPUT_REGISTER | 1529 | 1 |  | u8 | 0 | 0 | 0
Compressor, time to start (EB100-EP14) | MODBUS_INPUT_REGISTER | 1530 | 1 | min | u8 | 0 | 0 | 0
Relay status (EB100-EP14) | MODBUS_INPUT_REGISTER | 1531 | 1 |  | u16 | 0 | 0 | 0
Heating medium pump (EB100) | MODBUS_INPUT_REGISTER | 1532 | 1 | % | u8 | 0 | 0 | 0
Brine pump (EB100) | MODBUS_INPUT_REGISTER | 1533 | 1 | % | u8 | 0 | 0 | 0
Compressor, number of starts (EB100-EP14) | MODBUS_INPUT_REGISTER | 1534 | 1 |  | u32 | 0 | 0 | 0
Compressor, oper. time, total (EB100-EP14) | MODBUS_INPUT_REGISTER | 1536 | 1 | h | u32 | 0 | 0 | 0
Compressor, oper. time, hot water (EB100-EP14) | MODBUS_INPUT_REGISTER | 1538 | 1 | h | u32 | 0 | 0 | 0
Compressor, requested (EB108-EP15) | MODBUS_INPUT_REGISTER | 1541 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB108-EP14) | MODBUS_INPUT_REGISTER | 1542 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB107-EP15) | MODBUS_INPUT_REGISTER | 1543 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB107-EP14) | MODBUS_INPUT_REGISTER | 1544 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB106-EP15) | MODBUS_INPUT_REGISTER | 1545 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB106-EP14) | MODBUS_INPUT_REGISTER | 1546 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB105-EP15) | MODBUS_INPUT_REGISTER | 1547 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB105-EP14) | MODBUS_INPUT_REGISTER | 1548 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB104-EP15) | MODBUS_INPUT_REGISTER | 1549 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB104-EP14) | MODBUS_INPUT_REGISTER | 1550 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB103-EP15) | MODBUS_INPUT_REGISTER | 1551 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB103-EP14) | MODBUS_INPUT_REGISTER | 1552 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB102-EP15) | MODBUS_INPUT_REGISTER | 1553 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB102-EP14) | MODBUS_INPUT_REGISTER | 1554 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB101-EP15) | MODBUS_INPUT_REGISTER | 1555 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB101-EP14) | MODBUS_INPUT_REGISTER | 1556 | 1 |  | u8 | 0 | 0 | 0
Cooling blocking | MODBUS_INPUT_REGISTER | 1559 | 1 |  | u8 | 0 | 0 | 0
Date, periodic hot water | MODBUS_INPUT_REGISTER | 1561 | 1 |  | -
Blocked compressors | MODBUS_INPUT_REGISTER | 2174 | 1 |  | u32 | 0 | 0 | 0
Cooling degree minutes | MODBUS_HOLDING_REGISTER | 20 | 10 | DM | s16 | -30000 | 30000 | 0
Status (ACS) | MODBUS_INPUT_REGISTER | 1568 | 1 |  | u8 | 0 | 0 | 0
Status, heating dumping (ACS) | MODBUS_INPUT_REGISTER | 1569 | 1 |  | u8 | 0 | 0 | 0
Status, cooling dumping (ACS) | MODBUS_INPUT_REGISTER | 1570 | 1 |  | u8 | 0 | 0 | 0
Used compressors hot water | MODBUS_INPUT_REGISTER | 1571 | 1 |  | u8 | 0 | 0 | 0
Used compressors heating | MODBUS_INPUT_REGISTER | 1572 | 1 |  | u8 | 0 | 0 | 0
Used compressors pool 1 | MODBUS_INPUT_REGISTER | 1573 | 1 |  | u8 | 0 | 0 | 0
Used compressors pool 2 | MODBUS_INPUT_REGISTER | 1574 | 1 |  | u8 | 0 | 0 | 0
id:2728 | MODBUS_HOLDING_REGISTER | 3099 | 1 |  | s32 | 0 | 9999999 | 0
Used compressors cooling | MODBUS_INPUT_REGISTER | 1588 | 1 |  | u8 | 0 | 0 | 0
Outdoor temperature (EB101-BT28) | MODBUS_INPUT_REGISTER | 1621 | 10 | °C | s16 | 0 | 0 | 0
Evaporator (EB101-BT16) | MODBUS_INPUT_REGISTER | 1622 | 10 | °C | s16 | 0 | 0 | 0
(EB100-EP15-BT28) | MODBUS_INPUT_REGISTER | 1623 | 10 | °C | s16 | 0 | 0 | 0
(EB100-EP15-BT16) | MODBUS_INPUT_REGISTER | 1624 | 10 | °C | s16 | 0 | 0 | 0
(EB100-EP14-BT28) | MODBUS_INPUT_REGISTER | 1625 | 10 | °C | s16 | 0 | 0 | 0
(EB100-EP14-BT16) | MODBUS_INPUT_REGISTER | 1626 | 10 | °C | s16 | 0 | 0 | 0
Charge pump speed (EB101-GP12) | MODBUS_INPUT_REGISTER | 1636 | 1 | % | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 1 | MODBUS_INPUT_REGISTER | 1638 | 1 |  | u8 | 0 | 0 | 0
Bit register (EB100) | MODBUS_INPUT_REGISTER | 1687 | 1 |  | u8 | 0 | 0 | 0
Controlling hot water sensor (EB100-BT6) | MODBUS_INPUT_REGISTER | 1688 | 10 | °C | s16 | 0 | 0 | 0
Display hot water sensor (EB100-BT7) | MODBUS_INPUT_REGISTER | 1689 | 10 | °C | s16 | 0 | 0 | 0
Supply temperature sensor (EB100-BT2) | MODBUS_INPUT_REGISTER | 1690 | 10 | °C | s16 | 0 | 0 | 0
Compressor status (EB100-EP15) | MODBUS_INPUT_REGISTER | 1691 | 1 |  | u8 | 0 | 0 | 0
Compressor status (EB100-EP14) | MODBUS_INPUT_REGISTER | 1692 | 1 |  | u8 | 0 | 0 | 0
Operating mode extra additional heat | MODBUS_INPUT_REGISTER | 1693 | 1 |  | u8 | 0 | 0 | 0
Docked compressors cooling | MODBUS_INPUT_REGISTER | 1694 | 1 |  | u8 | 0 | 0 | 0
BP4, unprocessed (EB108-EP15) | MODBUS_INPUT_REGISTER | 1695 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB108-EP15--BP8) | MODBUS_INPUT_REGISTER | 1697 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB108-EP15) | MODBUS_INPUT_REGISTER | 1699 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB108-EP15) | MODBUS_INPUT_REGISTER | 1700 | 1 |  | u8 | 0 | 0 | 0
BP4, unprocessed (EB108-EP14) | MODBUS_INPUT_REGISTER | 1702 | 1 |  | s16 | 0 | 0 | 0
Defrosting (EB108) | MODBUS_INPUT_REGISTER | 1707 | 1 |  | u8 | 0 | 0 | 0
BP4, unprocessed (EB107-EP15) | MODBUS_INPUT_REGISTER | 1709 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB107-EP15--BP8) | MODBUS_INPUT_REGISTER | 1711 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB107-EP15) | MODBUS_INPUT_REGISTER | 1713 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB107-EP15) | MODBUS_INPUT_REGISTER | 1714 | 1 |  | u8 | 0 | 0 | 0
Power (EB107-EP15) | MODBUS_INPUT_REGISTER | 1715 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB107-EP14) | MODBUS_INPUT_REGISTER | 1716 | 1 |  | s16 | 0 | 0 | 0
Defrosting (EB107) | MODBUS_INPUT_REGISTER | 1721 | 1 |  | u8 | 0 | 0 | 0
Power (EB107-EP14) | MODBUS_INPUT_REGISTER | 1722 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB106-EP15) | MODBUS_INPUT_REGISTER | 1723 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB106-EP15--BP8) | MODBUS_INPUT_REGISTER | 1725 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB106-EP15) | MODBUS_INPUT_REGISTER | 1727 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB106-EP15) | MODBUS_INPUT_REGISTER | 1728 | 1 |  | u8 | 0 | 0 | 0
Power (EB106-EP15) | MODBUS_INPUT_REGISTER | 1729 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB106-EP14) | MODBUS_INPUT_REGISTER | 1730 | 1 |  | s16 | 0 | 0 | 0
Defrosting (EB106) | MODBUS_INPUT_REGISTER | 1735 | 1 |  | u8 | 0 | 0 | 0
Power (EB106-EP14) | MODBUS_INPUT_REGISTER | 1736 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB105-EP15) | MODBUS_INPUT_REGISTER | 1737 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB105-EP15--BP8) | MODBUS_INPUT_REGISTER | 1739 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB105-EP15) | MODBUS_INPUT_REGISTER | 1741 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB105-EP15) | MODBUS_INPUT_REGISTER | 1742 | 1 |  | u8 | 0 | 0 | 0
Power (EB105-EP15) | MODBUS_INPUT_REGISTER | 1743 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB105-EP14) | MODBUS_INPUT_REGISTER | 1744 | 1 |  | s16 | 0 | 0 | 0
Defrosting (EB105) | MODBUS_INPUT_REGISTER | 1749 | 1 |  | u8 | 0 | 0 | 0
Power (EB105-EP15) | MODBUS_INPUT_REGISTER | 1750 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB104-EP15) | MODBUS_INPUT_REGISTER | 1751 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB104-EP15--BP8) | MODBUS_INPUT_REGISTER | 1753 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB104-EP15) | MODBUS_INPUT_REGISTER | 1755 | 1 |  | u16 | 0 | 0 | 0
Low pressure (EB103-EP15--BP8) | MODBUS_INPUT_REGISTER | 1767 | 10 | bar | s16 | 0 | 0 | 0
BP4, unprocessed (EB103-EP14) | MODBUS_INPUT_REGISTER | 1772 | 1 |  | s16 | 0 | 0 | 0
Defrosting (EB103) | MODBUS_INPUT_REGISTER | 1777 | 1 |  | u8 | 0 | 0 | 0
Power (EB103-EP14) | MODBUS_INPUT_REGISTER | 1778 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB102-EP15) | MODBUS_INPUT_REGISTER | 1779 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB102-EP15--BP8) | MODBUS_INPUT_REGISTER | 1781 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB102-EP15) | MODBUS_INPUT_REGISTER | 1783 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB102-EP15) | MODBUS_INPUT_REGISTER | 1784 | 1 |  | u8 | 0 | 0 | 0
Power (EB102-EP15) | MODBUS_INPUT_REGISTER | 1785 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB102-EP14) | MODBUS_INPUT_REGISTER | 1786 | 1 |  | s16 | 0 | 0 | 0
Defrosting (EB102) | MODBUS_INPUT_REGISTER | 1791 | 1 |  | u8 | 0 | 0 | 0
Power (EB102-EP14) | MODBUS_INPUT_REGISTER | 1792 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB101-EP15) | MODBUS_INPUT_REGISTER | 1793 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB101-EP15-BP8) | MODBUS_INPUT_REGISTER | 1795 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB101-EP15) | MODBUS_INPUT_REGISTER | 1797 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB101-EP15) | MODBUS_INPUT_REGISTER | 1798 | 1 |  | u8 | 0 | 0 | 0
Power (EB101-EP15) | MODBUS_INPUT_REGISTER | 1799 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB101-EP14) | MODBUS_INPUT_REGISTER | 1800 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB101-BP8) | MODBUS_INPUT_REGISTER | 1802 | 10 | bar | s16 | 0 | 0 | 0
Current compressor frequency (EB101) | MODBUS_INPUT_REGISTER | 1803 | 10 | Hz | s16 | 0 | 0 | 0
Protection mode (EB101) | MODBUS_INPUT_REGISTER | 1804 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB101) | MODBUS_INPUT_REGISTER | 1805 | 1 |  | u8 | 0 | 0 | 0
Power (EB101-EP14) | MODBUS_INPUT_REGISTER | 1806 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB100-EP15) | MODBUS_INPUT_REGISTER | 1807 | 1 |  | s16 | 0 | 0 | 0
Pressure sensor, condenser (EB100-EP15-BP4) | MODBUS_INPUT_REGISTER | 1808 | 10 | bar | s16 | 0 | 0 | 0
Low pressure (EB100-EP15-BP8) | MODBUS_INPUT_REGISTER | 1809 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB100-EP15) | MODBUS_INPUT_REGISTER | 1811 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB100-EP15) | MODBUS_INPUT_REGISTER | 1812 | 1 |  | u8 | 0 | 0 | 0
Power (EB100-EP15) | MODBUS_INPUT_REGISTER | 1813 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB100-EP14) | MODBUS_INPUT_REGISTER | 1814 | 1 |  | s16 | 0 | 0 | 0
Pressure sensor, condenser (EB100-EP14-BP4) | MODBUS_INPUT_REGISTER | 1815 | 10 | bar | s16 | 0 | 0 | 0
Low pressure (EB100-EP14-BP8) | MODBUS_INPUT_REGISTER | 1816 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB100-EP14) | MODBUS_INPUT_REGISTER | 1818 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB100-EP14) | MODBUS_INPUT_REGISTER | 1819 | 1 |  | u8 | 0 | 0 | 0
Power (EB100-EP14) | MODBUS_INPUT_REGISTER | 1820 | 1 | kW | u8 | 0 | 0 | 0
Climate system 4 | MODBUS_INPUT_REGISTER | 1823 | 1 |  | u8 | 0 | 0 | 0
Climate system 3 | MODBUS_INPUT_REGISTER | 1824 | 1 |  | u8 | 0 | 0 | 0
Climate system 2 | MODBUS_INPUT_REGISTER | 1825 | 1 |  | u8 | 0 | 0 | 0
Climate system 1 (HMP) | MODBUS_INPUT_REGISTER | 1826 | 1 |  | u8 | 0 | 0 | 0
Pool 2 pump status | MODBUS_INPUT_REGISTER | 1827 | 1 |  | u8 | 0 | 0 | 0
Pool 1 pump status | MODBUS_INPUT_REGISTER | 1828 | 1 |  | u8 | 0 | 0 | 0
ACS EQ1-QN12 | MODBUS_INPUT_REGISTER | 1830 | 1 |  | u8 | 0 | 0 | 0
ACS EQ1-GP20 | MODBUS_INPUT_REGISTER | 1831 | 1 |  | u8 | 0 | 0 | 0
Passive cooling pump (GP13) | MODBUS_INPUT_REGISTER | 1833 | 1 |  | u8 | 0 | 0 | 0
Oper. mode groundwater pump | MODBUS_INPUT_REGISTER | 1835 | 1 |  | u8 | 0 | 0 | 0
Alarm number (EB100-EP15) | MODBUS_INPUT_REGISTER | 1837 | 1 |  | u16 | 0 | 0 | 0
Alarm number (EB100-EP14) | MODBUS_INPUT_REGISTER | 1838 | 1 |  | u16 | 0 | 0 | 0
Requested compressor frequency (EB108-EP15) | MODBUS_INPUT_REGISTER | 1839 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB107-EP15) | MODBUS_INPUT_REGISTER | 1841 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB106-EP15) | MODBUS_INPUT_REGISTER | 1843 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB105-EP15) | MODBUS_INPUT_REGISTER | 1845 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB104-EP15) | MODBUS_INPUT_REGISTER | 1847 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB103-EP15) | MODBUS_INPUT_REGISTER | 1849 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB102-EP15) | MODBUS_INPUT_REGISTER | 1851 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB101-EP15) | MODBUS_INPUT_REGISTER | 1853 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB101) | MODBUS_INPUT_REGISTER | 1854 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EP15) | MODBUS_INPUT_REGISTER | 1855 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency | MODBUS_INPUT_REGISTER | 1856 | 1 | Hz | u8 | 0 | 0 | 0
Operating mode, shunt controlled brine (QN41) | MODBUS_INPUT_REGISTER | 2410 | 1 |  | u8 | 0 | 0 | 0
Low press. sensor, unprocessed (EB101-EP14) | MODBUS_INPUT_REGISTER | 1902 | 1 |  | s16 | 0 | 0 | 0
Current sensor (EB101-EP14) | MODBUS_INPUT_REGISTER | 1903 | 10 | A | s16 | 0 | 0 | 0
Low press. sensor, unprocessed (EB100-EP15) | MODBUS_INPUT_REGISTER | 1905 | 1 |  | s16 | 0 | 0 | 0
Current sensor (EB100-EP15) | MODBUS_INPUT_REGISTER | 1906 | 10 | A | s16 | 0 | 0 | 0
Low press. sensor, unprocessed (EB100-EP14) | MODBUS_INPUT_REGISTER | 1908 | 1 |  | s16 | 0 | 0 | 0
Current sensor (EB100-EP14) | MODBUS_INPUT_REGISTER | 1909 | 10 | A | s16 | 0 | 0 | 0
Operating mode (SG Ready) | MODBUS_INPUT_REGISTER | 1911 | 1 |  | u8 | 0 | 0 | 0
SG ready, input A | MODBUS_INPUT_REGISTER | 1912 | 1 |  | u8 | 0 | 0 | 0
SG ready, input B | MODBUS_INPUT_REGISTER | 1913 | 1 |  | u8 | 0 | 0 | 0
Hot water comfort mode (SPA) | MODBUS_INPUT_REGISTER | 1915 | 1 |  | s8 | 0 | 0 | 0
Pool offset (SPA) | MODBUS_INPUT_REGISTER | 1916 | 1 |  | s8 | 0 | 0 | 0
Cooling offset (SPA) | MODBUS_INPUT_REGISTER | 1917 | 1 |  | s8 | 0 | 0 | 0
Operating mode (Smart Price Adaption) | MODBUS_INPUT_REGISTER | 1918 | 1 |  | u8 | 0 | 0 | 0
Evaporator 2 (EB101-EP14-BT16) | MODBUS_INPUT_REGISTER | 1966 | 10 | °C | s16 | 0 | 0 | 0
Temperature, inverter (EB101-EP14) | MODBUS_INPUT_REGISTER | 1967 | 10 | °C | s16 | 0 | 0 | 0
fan speed (EB101-EP14) | MODBUS_INPUT_REGISTER | 1968 | 1 |  | u8 | 0 | 0 | 0
Evaporator 2 (EB100-EP15-BT16) | MODBUS_INPUT_REGISTER | 1969 | 10 | °C | s16 | 0 | 0 | 0
Temperature, inverter (EB100-EP15) | MODBUS_INPUT_REGISTER | 1970 | 10 | °C | s16 | 0 | 0 | 0
fan speed (EB100-EP15) | MODBUS_INPUT_REGISTER | 1971 | 1 |  | u8 | 0 | 0 | 0
Evaporator 2 (EB100-EP14-BT16) | MODBUS_INPUT_REGISTER | 1972 | 10 | °C | s16 | 0 | 0 | 0
Temperature, inverter (EB100-EP14) | MODBUS_INPUT_REGISTER | 1973 | 10 | °C | s16 | 0 | 0 | 0
fan speed (EB100-EP14) | MODBUS_INPUT_REGISTER | 1974 | 1 |  | u8 | 0 | 0 | 0
Alarm number | MODBUS_INPUT_REGISTER | 1975 | 1 |  | s16 | 0 | 0 | 0
Reset alarm | MODBUS_HOLDING_REGISTER | 22 | 1 |  | u8 | 0 | 0 | 0
Non module-specific alarm numbers | MODBUS_INPUT_REGISTER | 1976 | 1 |  | s16 | 0 | 0 | 0
Heating curve climate system 1 | MODBUS_HOLDING_REGISTER | 26 | 1 |  | s8 | 0 | 15 | 9
Heating offset climate system 1 | MODBUS_HOLDING_REGISTER | 30 | 1 |  | s8 | -10 | 10 | 0
Min supply climate system 1 | MODBUS_HOLDING_REGISTER | 34 | 10 | °C | s16 | 50 | 800 | 200
Max supply climate system 1 | MODBUS_HOLDING_REGISTER | 38 | 10 | °C | s16 | 50 | 800 | 600
Own curve, heating P7 | MODBUS_HOLDING_REGISTER | 39 | 1 | °C | s8 | 5 | 80 | 15
Own curve, heating P6 | MODBUS_HOLDING_REGISTER | 40 | 1 | °C | s8 | 5 | 80 | 15
Own curve, heating P5 | MODBUS_HOLDING_REGISTER | 41 | 1 | °C | s8 | 5 | 80 | 26
Own curve, heating P4 | MODBUS_HOLDING_REGISTER | 42 | 1 | °C | s8 | 5 | 80 | 32
Own curve, heating P3 | MODBUS_HOLDING_REGISTER | 43 | 1 | °C | s8 | 5 | 80 | 35
Own curve, heating P2 | MODBUS_HOLDING_REGISTER | 44 | 1 | °C | s8 | 5 | 80 | 40
Own curve, heating P1 | MODBUS_HOLDING_REGISTER | 45 | 1 | °C | s8 | 5 | 80 | 45
Point offset outdoor temperature | MODBUS_HOLDING_REGISTER | 46 | 1 | °C | s8 | -40 | 30 | 0
Point offset | MODBUS_HOLDING_REGISTER | 47 | 1 | °C | s8 | -10 | 10 | 0
External adjustment climate system 1 | MODBUS_HOLDING_REGISTER | 51 | 1 |  | s8 | -10 | 10 | 0
External adjustment with room sensor climate system 1 | MODBUS_HOLDING_REGISTER | 55 | 10 | °C | s16 | 50 | 300 | 200
Stop temperature HW periodic increase | MODBUS_HOLDING_REGISTER | 61 | 10 | °C | s16 | 550 | 700 | 550
Periodic hot water | MODBUS_HOLDING_REGISTER | 65 | 1 |  | s8 | 0 | 1 | 1
Periodic hot water interval | MODBUS_HOLDING_REGISTER | 66 | 1 | days | s8 | 1 | 90 | 7
Start time periodic hot water | MODBUS_HOLDING_REGISTER | 67 | 1 |  | -
Language | MODBUS_HOLDING_REGISTER | 91 | 1 |  | s8 | 0 | 24 | 0
Operating mode | MODBUS_HOLDING_REGISTER | 2743 | 1 |  | u8 | 0 | 2 | 0
Operating mode heating medium pump | MODBUS_HOLDING_REGISTER | 95 | 1 |  | u8 | 10 | 40 | 40
Activate forced control | MODBUS_HOLDING_REGISTER | 5000 | 1 |  | u8 | 0 | 0 | 0
Fuse | MODBUS_HOLDING_REGISTER | 103 | 1 | A | u16 | 1 | 400 | 32
Phase Order L3 | MODBUS_HOLDING_REGISTER | 2747 | 1 |  | u8 | 1 | 128 | 4
Phase Order L2 | MODBUS_HOLDING_REGISTER | 2746 | 1 |  | u8 | 1 | 128 | 2
Phase Order L1 | MODBUS_HOLDING_REGISTER | 2745 | 1 |  | u8 | 1 | 128 | 1
Floor drying | MODBUS_HOLDING_REGISTER | 120 | 1 |  | u8 | 0 | 1 | 0
Floor drying period 7 | MODBUS_HOLDING_REGISTER | 121 | 1 | days | u8 | 0 | 30 | 2
Floor drying period 6 | MODBUS_HOLDING_REGISTER | 122 | 1 | days | u8 | 0 | 30 | 2
Floor drying period 5 | MODBUS_HOLDING_REGISTER | 123 | 1 | days | u8 | 0 | 30 | 2
Floor drying period 4 | MODBUS_HOLDING_REGISTER | 124 | 1 | days | u8 | 0 | 30 | 3
Floor drying period 3 | MODBUS_HOLDING_REGISTER | 125 | 1 | days | u8 | 0 | 30 | 2
Floor drying period 2 | MODBUS_HOLDING_REGISTER | 126 | 1 | days | u8 | 0 | 30 | 2
Floor drying period 1 | MODBUS_HOLDING_REGISTER | 127 | 1 | days | u8 | 0 | 30 | 2
Floor drying temp. 7 | MODBUS_HOLDING_REGISTER | 128 | 1 | °C | u8 | 15 | 70 | 20
Floor drying temp. 6 | MODBUS_HOLDING_REGISTER | 129 | 1 | °C | u8 | 15 | 70 | 30
Floor drying temp. 5 | MODBUS_HOLDING_REGISTER | 130 | 1 | °C | u8 | 15 | 70 | 40
Floor drying temp. 4 | MODBUS_HOLDING_REGISTER | 131 | 1 | °C | u8 | 15 | 70 | 45
Floor drying temp. 3 | MODBUS_HOLDING_REGISTER | 132 | 1 | °C | u8 | 15 | 70 | 40
Floor drying temp. 2 | MODBUS_HOLDING_REGISTER | 133 | 1 | °C | u8 | 15 | 70 | 30
Floor drying temp. 1 | MODBUS_HOLDING_REGISTER | 134 | 1 | °C | u8 | 15 | 70 | 20
Floor drying ongoing time. | MODBUS_INPUT_REGISTER | 1977 | 1 |  | u16 | 0 | 10000 | 0
Dimensioned outdoor temperature | MODBUS_HOLDING_REGISTER | 140 | 10 | °C | s16 | -400 | 200 | -180
Delta T for DOT | MODBUS_HOLDING_REGISTER | 141 | 10 | °C | s16 | 10 | 250 | 100
Climate system 2 | MODBUS_HOLDING_REGISTER | 142 | 1 |  | u8 | 0 | 1 | 0
Climate system 3 | MODBUS_HOLDING_REGISTER | 143 | 1 |  | u8 | 0 | 1 | 0
Climate system 4 | MODBUS_HOLDING_REGISTER | 144 | 1 |  | u8 | 0 | 1 | 0
Shunt controlled additional heat | MODBUS_HOLDING_REGISTER | 153 | 1 |  | u8 | 0 | 1 | 0
Wait time shunt, shunt controlled additional heat | MODBUS_HOLDING_REGISTER | 157 | 1 | s | s16 | 10 | 300 | 30
Step controlled additional heat accessory | MODBUS_HOLDING_REGISTER | 158 | 1 |  | u8 | 0 | 1 | 0
Ground water pump accessory | MODBUS_HOLDING_REGISTER | 162 | 1 |  | u8 | 0 | 1 | 0
Waiting time cooling/heating | MODBUS_HOLDING_REGISTER | 165 | 1 | h | s8 | 0 | 48 | 2
Heating start at under temp. | MODBUS_HOLDING_REGISTER | 166 | 10 | °C | s8 | 5 | 100 | 10
Cooling start at over temp. | MODBUS_HOLDING_REGISTER | 167 | 10 | °C | s8 | 5 | 100 | 30
Cooling shunt amplification | MODBUS_HOLDING_REGISTER | 168 | 10 |  | s8 | 1 | 100 | 10
Cooling shunt waiting time | MODBUS_HOLDING_REGISTER | 169 | 1 | s | s16 | 10 | 300 | 30
Cooling with room sensors | MODBUS_HOLDING_REGISTER | 170 | 10 |  | u8 | 0 | 41 | 0
Start passive cooling DM | MODBUS_HOLDING_REGISTER | 172 | 1 | DM | s16 | 10 | 500 | 30
Start active cooling DM | MODBUS_HOLDING_REGISTER | 173 | 1 | DM | s16 | 10 | 300 | 30
Changes have been made | MODBUS_HOLDING_REGISTER | 2744 | 1 |  | u8 | 0 | 1 | 0
Permit additional heat, heating | MODBUS_HOLDING_REGISTER | 180 | 1 |  | u8 | 0 | 1 | 1
Permit heating | MODBUS_HOLDING_REGISTER | 181 | 1 |  | u8 | 0 | 1 | 1
Permit cooling | MODBUS_HOLDING_REGISTER | 182 | 1 |  | u8 | 0 | 1 | 1
Auto mode, stop temperature for heating | MODBUS_HOLDING_REGISTER | 184 | 10 | °C | s16 | -200 | 400 | 170
Auto mode, additional heat stop temperature | MODBUS_HOLDING_REGISTER | 185 | 10 | °C | s16 | -250 | 400 | 50
Auto mode filter time | MODBUS_HOLDING_REGISTER | 186 | 1 | h | u8 | 0 | 48 | 24
Max difference supply, compressor | MODBUS_HOLDING_REGISTER | 187 | 10 | °C | s16 | 10 | 250 | 100
Max difference supply, additional heat | MODBUS_HOLDING_REGISTER | 188 | 10 | °C | s16 | 10 | 240 | 70
Time format | MODBUS_HOLDING_REGISTER | 194 | 1 |  | u8 | 0 | 1 | 1
Hot water permitted | MODBUS_HOLDING_REGISTER | 195 | 1 |  | u8 | 0 | 1 | 0
Alarm action, lower room temperature | MODBUS_HOLDING_REGISTER | 196 | 1 |  | u8 | 0 | 1 | 0
Auxiliary operation on alarm | MODBUS_HOLDING_REGISTER | 198 | 1 |  | u8 | 0 | 0 | 0
Use room sensor climate system 4 | MODBUS_HOLDING_REGISTER | 199 | 1 |  | u8 | 0 | 1 | 0
Use room sensor climate system 3 | MODBUS_HOLDING_REGISTER | 200 | 1 |  | u8 | 0 | 1 | 0
Use room sensor climate system 2 | MODBUS_HOLDING_REGISTER | 201 | 1 |  | u8 | 0 | 1 | 0
Use room sensor climate system 1 | MODBUS_HOLDING_REGISTER | 202 | 1 |  | u8 | 0 | 1 | 0
Room sensor set point value climate system 4 | MODBUS_HOLDING_REGISTER | 203 | 10 | °C | s16 | 50 | 300 | 200
Room sensor set point value climate system 3 | MODBUS_HOLDING_REGISTER | 204 | 10 | °C | s16 | 50 | 300 | 200
Room sensor set point value climate system 2 | MODBUS_HOLDING_REGISTER | 205 | 10 | °C | s16 | 50 | 300 | 200
Room sensor set point value climate system 1 | MODBUS_HOLDING_REGISTER | 206 | 10 | °C | s16 | 50 | 300 | 200
Room sensor factor climate system 4 | MODBUS_HOLDING_REGISTER | 207 | 10 |  | u8 | 0 | 60 | 20
Room sensor factor climate system 3 | MODBUS_HOLDING_REGISTER | 208 | 10 |  | u8 | 0 | 60 | 20
Room sensor factor climate system 2 | MODBUS_HOLDING_REGISTER | 209 | 10 |  | u8 | 0 | 60 | 20
Room sensor factor climate system 1 | MODBUS_HOLDING_REGISTER | 210 | 10 |  | u8 | 0 | 60 | 20
Input AUX5 | MODBUS_HOLDING_REGISTER | 211 | 1 |  | u8 | 0 | 68 | 0
Input AUX4 | MODBUS_HOLDING_REGISTER | 212 | 1 |  | u8 | 0 | 68 | 0
Input AUX3 | MODBUS_HOLDING_REGISTER | 213 | 1 |  | u8 | 0 | 68 | 0
Input AUX2 | MODBUS_HOLDING_REGISTER | 214 | 1 |  | u8 | 0 | 68 | 0
Input AUX1 | MODBUS_HOLDING_REGISTER | 215 | 1 |  | u8 | 0 | 68 | 0
Output AUX1 | MODBUS_HOLDING_REGISTER | 216 | 1 |  | u8 | 0 | 30 | 0
Speed, brine pump | MODBUS_HOLDING_REGISTER | 222 | 1 | % | u8 | 1 | 100 | 100
id:3968 | MODBUS_HOLDING_REGISTER | 2752 | 1 |  | u16 | 1 | 3600 | 5
Preset flow setting for climate system | MODBUS_HOLDING_REGISTER | 223 | 1 |  | u8 | 0 | 3 | 1
id:3977 | MODBUS_HOLDING_REGISTER | 2753 | 1 |  | u8 | 21 | 22 | 21
More hot water (Number of minutes) | MODBUS_HOLDING_REGISTER | 225 | 1 |  | u16 | 0 | 0 | 0
id:4045 | MODBUS_HOLDING_REGISTER | 5245 | 1 | °C | s8 | 1 | 40 | 8
id:4046 | MODBUS_HOLDING_REGISTER | 5247 | 1 | °C | s8 | 0 | 40 | 4
id:4049 | MODBUS_HOLDING_REGISTER | 5249 | 1 |  | u8 | 0 | 1 | 0
id:4050 | MODBUS_HOLDING_REGISTER | 5250 | 1 |  | u8 | 0 | 1 | 0
id:4051 | MODBUS_HOLDING_REGISTER | 5251 | 1 |  | u8 | 0 | 1 | 0
Oper. mode | MODBUS_HOLDING_REGISTER | 237 | 1 |  | u8 | 0 | 0 | 0
Max. step internal additional heat | MODBUS_HOLDING_REGISTER | 238 | 1 |  | u8 | 0 | 7 | 3
Internal additional heat stepping mode | MODBUS_HOLDING_REGISTER | 239 | 1 |  | u8 | 0 | 1 | 0
Cooling heat sensor set point value | MODBUS_HOLDING_REGISTER | 681 | 10 |  | s16 | 50 | 400 | 210
Heating medium pump manual speed | MODBUS_HOLDING_REGISTER | 682 | 1 | % | s8 | 1 | 100 | 70
Pool 2 accessory | MODBUS_HOLDING_REGISTER | 684 | 1 |  | u8 | 0 | 1 | 0
Pool 1 accessory | MODBUS_HOLDING_REGISTER | 685 | 1 |  | u8 | 0 | 1 | 0
Hot water comfort | MODBUS_HOLDING_REGISTER | 694 | 1 |  | u8 | 0 | 1 | 0
Manual heating medium pump speed | MODBUS_HOLDING_REGISTER | 695 | 1 | % | s8 | 0 | 1 | 0
More hot water | MODBUS_HOLDING_REGISTER | 697 | 1 |  | s8 | 0 | 0 | 0
Start diff. DM, step-controlled add. heat | MODBUS_HOLDING_REGISTER | 703 | 1 | DM | s16 | 0 | 2000 | 400
HW comfort shunt on/off | MODBUS_HOLDING_REGISTER | 705 | 1 |  | u8 | 0 | 1 | 0
External cooling accessory | MODBUS_HOLDING_REGISTER | 709 | 1 |  | u8 | 0 | 1 | 0
HW comfort additional heat | MODBUS_HOLDING_REGISTER | 710 | 1 |  | u8 | 0 | 1 | 0
id:4591 | MODBUS_HOLDING_REGISTER | 5256 | 1 |  | s8 | 5 | 80 | 30
Cooling connected, climate system 1 | MODBUS_HOLDING_REGISTER | 726 | 1 |  | u8 | 0 | 1 | 1
ACS | MODBUS_HOLDING_REGISTER | 731 | 1 |  | u8 | 0 | 1 | 0
id:4617 | MODBUS_HOLDING_REGISTER | 5257 | 1 |  | s8 | 0 | 1 | 0
Op. mode charge pump (EB101) | MODBUS_HOLDING_REGISTER | 748 | 1 |  | u8 | 0 | 1 | 0
id:4660 | MODBUS_HOLDING_REGISTER | 5267 | 1 |  | u8 | 0 | 0 | 0
Shunted brine, accessory | MODBUS_HOLDING_REGISTER | 5268 | 1 |  | u8 | 0 | 1 | 0
Shunted brine max. temp. | MODBUS_HOLDING_REGISTER | 5271 | 1 | °C | u8 | 0 | 30 | 20
Hot water compressors step diff. | MODBUS_HOLDING_REGISTER | 755 | 100 |  | s16 | 0 | 400 | 100
Additional heat after reversing valve | MODBUS_HOLDING_REGISTER | 758 | 1 |  | u8 | 0 | 1 | 1
Heating (SG Ready) | MODBUS_HOLDING_REGISTER | 760 | 1 |  | u8 | 0 | 1 | 1
id:4703 | MODBUS_HOLDING_REGISTER | 5272 | 1 |  | u8 | 0 | 1 | 0
id:4704 | MODBUS_HOLDING_REGISTER | 5273 | 1 |  | u8 | 0 | 1 | 0
id:4705 | MODBUS_HOLDING_REGISTER | 5274 | 1 |  | u8 | 0 | 1 | 0
id:4706 | MODBUS_HOLDING_REGISTER | 5275 | 1 |  | u8 | 0 | 1 | 0
id:4707 | MODBUS_HOLDING_REGISTER | 5276 | 1 |  | u8 | 0 | 1 | 0
id:4708 | MODBUS_HOLDING_REGISTER | 5277 | 1 |  | u8 | 0 | 1 | 0
id:4709 | MODBUS_HOLDING_REGISTER | 5278 | 1 |  | u8 | 0 | 1 | 0
id:4710 | MODBUS_HOLDING_REGISTER | 5279 | 1 |  | u8 | 0 | 1 | 0
Input AUX6 | MODBUS_HOLDING_REGISTER | 767 | 1 |  | u8 | 0 | 68 | 0
Operating mode circulation pump heating heat pump 1 | MODBUS_HOLDING_REGISTER | 783 | 1 |  | u8 | 0 | 1 | 1
Speed circulation pump waiting mode heat pump 1 | MODBUS_HOLDING_REGISTER | 841 | 1 | % | u8 | 1 | 100 | 30
Speed, circulation pump, standby mode (EB100) | MODBUS_HOLDING_REGISTER | 842 | 1 | % | u8 | 1 | 100 | 30
Activated (Smart Price Adaption) | MODBUS_HOLDING_REGISTER | 843 | 1 |  | u8 | 0 | 1 | 0
(SPA), cooling activated | MODBUS_HOLDING_REGISTER | 849 | 1 |  | u8 | 0 | 1 | 1
(SPA), area | MODBUS_HOLDING_REGISTER | 851 | 1 |  | u8 | 0 | 255 | 255
Internal shunt controlled additional heat | MODBUS_HOLDING_REGISTER | 857 | 1 |  | u8 | 0 | 1 | 0
Max. speed controlled charge pump (EB101) | MODBUS_HOLDING_REGISTER | 867 | 1 | % | u8 | 80 | 100 | 100
External adjustment climate system 8 | MODBUS_HOLDING_REGISTER | 893 | 1 |  | s8 | -10 | 10 | 0
External adjustment climate system 7 | MODBUS_HOLDING_REGISTER | 894 | 1 |  | s8 | -10 | 10 | 0
External adjustment climate system 6 | MODBUS_HOLDING_REGISTER | 895 | 1 |  | s8 | -10 | 10 | 0
External adjustment climate system 5 | MODBUS_HOLDING_REGISTER | 896 | 1 |  | s8 | -10 | 10 | 0
External adjustment with room sensor climate system 8 | MODBUS_HOLDING_REGISTER | 897 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor climate system 7 | MODBUS_HOLDING_REGISTER | 898 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor climate system 6 | MODBUS_HOLDING_REGISTER | 899 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor climate system 5 | MODBUS_HOLDING_REGISTER | 900 | 10 | °C | s16 | 50 | 300 | 200
Climate system 5 | MODBUS_HOLDING_REGISTER | 905 | 1 |  | u8 | 0 | 1 | 0
Climate system 6 | MODBUS_HOLDING_REGISTER | 906 | 1 |  | u8 | 0 | 1 | 0
Climate system 7 | MODBUS_HOLDING_REGISTER | 907 | 1 |  | u8 | 0 | 1 | 0
Climate system 8 | MODBUS_HOLDING_REGISTER | 908 | 1 |  | u8 | 0 | 1 | 0
Heating connected, climate system 1 | MODBUS_HOLDING_REGISTER | 932 | 1 |  | u8 | 0 | 1 | 1
ERS 1 | MODBUS_HOLDING_REGISTER | 933 | 1 |  | u8 | 0 | 1 | 0
EB103/104-GP12 | MODBUS_HOLDING_REGISTER | 939 | 1 |  | u8 | 0 | 1 | 0
EB105/106-GP12 | MODBUS_HOLDING_REGISTER | 940 | 1 |  | u8 | 0 | 1 | 0
EB107/108-GP12 | MODBUS_HOLDING_REGISTER | 941 | 1 |  | u8 | 0 | 1 | 0
blockFreq 2 (EB101) | MODBUS_HOLDING_REGISTER | 5295 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB101) | MODBUS_HOLDING_REGISTER | 5296 | 1 |  | u8 | 0 | 1 | 0
id:4971 | MODBUS_HOLDING_REGISTER | 5297 | 1 | Hz | u8 | 20 | 117 | 20
id:4972 | MODBUS_HOLDING_REGISTER | 5298 | 1 | Hz | u8 | 20 | 117 | 20
id:4973 | MODBUS_HOLDING_REGISTER | 5299 | 1 | Hz | u8 | 23 | 120 | 23
id:4974 | MODBUS_HOLDING_REGISTER | 5300 | 1 | Hz | u8 | 23 | 120 | 23
Use room sensor climate system 8 | MODBUS_HOLDING_REGISTER | 948 | 1 |  | u8 | 0 | 1 | 0
Use room sensor climate system 7 | MODBUS_HOLDING_REGISTER | 949 | 1 |  | u8 | 0 | 1 | 0
Use room sensor climate system 6 | MODBUS_HOLDING_REGISTER | 950 | 1 |  | u8 | 0 | 1 | 0
Use room sensor climate system 5 | MODBUS_HOLDING_REGISTER | 951 | 1 |  | u8 | 0 | 1 | 0
Room sensor set point value climate system 8 | MODBUS_HOLDING_REGISTER | 952 | 10 | °C | s16 | 50 | 300 | 200
Room sensor set point value climate system 7 | MODBUS_HOLDING_REGISTER | 953 | 10 | °C | s16 | 50 | 300 | 200
Room sensor set point value climate system 6 | MODBUS_HOLDING_REGISTER | 954 | 10 | °C | s16 | 50 | 300 | 200
Room sensor set point value climate system 5 | MODBUS_HOLDING_REGISTER | 955 | 10 | °C | s16 | 50 | 300 | 200
Room sensor factor climate system 8 | MODBUS_HOLDING_REGISTER | 956 | 10 |  | u8 | 0 | 60 | 20
Room sensor factor climate system 7 | MODBUS_HOLDING_REGISTER | 957 | 10 |  | u8 | 0 | 60 | 20
Room sensor factor climate system 6 | MODBUS_HOLDING_REGISTER | 958 | 10 |  | u8 | 0 | 60 | 20
Room sensor factor climate system 5 | MODBUS_HOLDING_REGISTER | 959 | 10 |  | u8 | 0 | 60 | 20
Current transformer ratio | MODBUS_HOLDING_REGISTER | 980 | 1 |  | u16 | 300 | 3000 | 300
Room sensor set point value climate system 8, cooling | MODBUS_HOLDING_REGISTER | 981 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 7, cooling | MODBUS_HOLDING_REGISTER | 982 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 6, cooling | MODBUS_HOLDING_REGISTER | 983 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 5, cooling | MODBUS_HOLDING_REGISTER | 984 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 4, cooling | MODBUS_HOLDING_REGISTER | 985 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 3, cooling | MODBUS_HOLDING_REGISTER | 986 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 2, cooling | MODBUS_HOLDING_REGISTER | 987 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 1, cooling | MODBUS_HOLDING_REGISTER | 988 | 10 | °C | s16 | 50 | 350 | 250
Room sensor factor climate system 8, cooling | MODBUS_HOLDING_REGISTER | 989 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 7, cooling | MODBUS_HOLDING_REGISTER | 990 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 6, cooling | MODBUS_HOLDING_REGISTER | 991 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 5, cooling | MODBUS_HOLDING_REGISTER | 992 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 4, cooling | MODBUS_HOLDING_REGISTER | 993 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 3, cooling | MODBUS_HOLDING_REGISTER | 994 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 2, cooling | MODBUS_HOLDING_REGISTER | 995 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 1, cooling | MODBUS_HOLDING_REGISTER | 996 | 10 |  | u8 | 0 | 60 | 10
Set point value (RH) | MODBUS_HOLDING_REGISTER | 997 | 1 | % | s8 | 30 | 90 | 60
HTS 1 | MODBUS_HOLDING_REGISTER | 998 | 1 |  | u8 | 0 | 1 | 0
OPT | MODBUS_HOLDING_REGISTER | 1015 | 1 |  | u8 | 0 | 1 | 0
DM start difference (OPT) | MODBUS_HOLDING_REGISTER | 1016 | 1 | DM | s16 | 10 | 2000 | 700
Exhaust air fan speed 4 (ERS 1) | MODBUS_HOLDING_REGISTER | 1021 | 1 | % | u8 | 0 | 100 | 100
Exhaust air fan speed 3 (ERS 1) | MODBUS_HOLDING_REGISTER | 1022 | 1 | % | u8 | 0 | 100 | 80
Exhaust air fan speed 2 (ERS 1) | MODBUS_HOLDING_REGISTER | 1023 | 1 | % | u8 | 0 | 100 | 30
Exhaust air fan speed 1 (ERS 1) | MODBUS_HOLDING_REGISTER | 1024 | 1 | % | u8 | 0 | 100 | 0
Exhaust air fan speed normal (ERS 1) | MODBUS_HOLDING_REGISTER | 1025 | 1 | % | u8 | 1 | 100 | 75
Filtering time (BT64) | MODBUS_HOLDING_REGISTER | 1027 | 1 | min | u8 | 5 | 30 | 5
(ACS) - Thermostat, hysteresis between compressors | MODBUS_HOLDING_REGISTER | 1028 | 1 | °C | s8 | 1 | 10 | 2
Start temperature (BT64) | MODBUS_HOLDING_REGISTER | 1029 | 1 | °C | s8 | -8 | 30 | 10
S135 | MODBUS_HOLDING_REGISTER | 1035 | 1 |  | u8 | 0 | 1 | 0
Pump speed (S135) | MODBUS_HOLDING_REGISTER | 1036 | 1 | % | u8 | 1 | 100 | 70
Bypass temp. (ERS 1) | MODBUS_HOLDING_REGISTER | 1044 | 1 | °C | u8 | 2 | 10 | 4
External cooling accessory pump type | MODBUS_HOLDING_REGISTER | 1046 | 1 |  | u8 | 0 | 1 | 1
Flow sensor activated X22 | MODBUS_HOLDING_REGISTER | 1049 | 1 |  | u8 | 0 | 1 | 0
Flow sensor activated X21 | MODBUS_HOLDING_REGISTER | 1050 | 1 |  | u8 | 0 | 1 | 0
Max. internal additional heat SG Ready | MODBUS_HOLDING_REGISTER | 1052 | 100 | kW | s16 | 0 | 900 | 700
Hysteresis (OPT) | MODBUS_HOLDING_REGISTER | 1066 | 1 |  | s16 | 10 | 2000 | 100
PV panel affects heating (EME) | MODBUS_HOLDING_REGISTER | 1069 | 1 |  | u8 | 0 | 1 | 0
PV panel affects hot water (EME) | MODBUS_HOLDING_REGISTER | 1070 | 1 |  | u8 | 0 | 1 | 0
Delay timer EME | MODBUS_HOLDING_REGISTER | 1071 | 1 |  | u16 | 0 | 0 | 0
Pump 4 (FLM) | MODBUS_HOLDING_REGISTER | 1074 | 1 |  | u8 | 0 | 1 | 0
Pump 3 (FLM) | MODBUS_HOLDING_REGISTER | 1075 | 1 |  | u8 | 0 | 1 | 0
Pump 2 (FLM) | MODBUS_HOLDING_REGISTER | 1076 | 1 |  | u8 | 0 | 1 | 0
Defrosting time (FLM 4) | MODBUS_HOLDING_REGISTER | 1077 | 1 | h | u8 | 1 | 30 | 10
Defrosting time (FLM 3) | MODBUS_HOLDING_REGISTER | 1078 | 1 | h | u8 | 1 | 30 | 10
Defrosting time (FLM 2) | MODBUS_HOLDING_REGISTER | 1079 | 1 | h | u8 | 1 | 30 | 10
Cooling (FLM 4) | MODBUS_HOLDING_REGISTER | 1080 | 1 |  | u8 | 0 | 1 | 0
Cooling (FLM 3) | MODBUS_HOLDING_REGISTER | 1081 | 1 |  | u8 | 0 | 1 | 0
Cooling (FLM 2) | MODBUS_HOLDING_REGISTER | 1082 | 1 |  | u8 | 0 | 1 | 0
Pump speed (FLM 4) | MODBUS_HOLDING_REGISTER | 1083 | 1 | % | u8 | 1 | 100 | 100
Pump speed (FLM 3) | MODBUS_HOLDING_REGISTER | 1084 | 1 | % | u8 | 1 | 100 | 100
Pump speed (FLM 2) | MODBUS_HOLDING_REGISTER | 1085 | 1 | % | u8 | 1 | 100 | 100
Pump speed (FLM 1) | MODBUS_HOLDING_REGISTER | 1086 | 1 | % | u8 | 1 | 100 | 100
AUX blocking (OPT) | MODBUS_HOLDING_REGISTER | 1095 | 1 |  | u8 | 0 | 0 | 0
Outdoor air mixing | MODBUS_HOLDING_REGISTER | 1096 | 1 |  | u8 | 0 | 1 | 0
Smart home room control | MODBUS_HOLDING_REGISTER | 1102 | 1 |  | u8 | 0 | 1 | 0
Smart Energy Source | MODBUS_HOLDING_REGISTER | 1105 | 1 |  | u8 | 0 | 1 | 0
Control method, smart energy source | MODBUS_HOLDING_REGISTER | 1106 | 1 |  | u8 | 0 | 1 | 0
El. price, special, smart energy source | MODBUS_HOLDING_REGISTER | 1107 | 1 |  | u8 | 0 | 2 | 0
El. price, fixed, smart energy source | MODBUS_HOLDING_REGISTER | 1108 | 1 |  | u16 | 0 | 10000 | 100
El. price, smart energy source | MODBUS_HOLDING_REGISTER | 1109 | 1 |  | u8 | 0 | 1 | 0
El. price, fixed, smart energy source | MODBUS_HOLDING_REGISTER | 1110 | 1 |  | u16 | 0 | 10000 | 100
El. price, smart energy source | MODBUS_HOLDING_REGISTER | 1111 | 1 |  | u8 | 0 | 3 | 0
El. price, fixed, smart energy source | MODBUS_HOLDING_REGISTER | 1112 | 1 |  | u16 | 0 | 10000 | 100
El. price, smart energy source | MODBUS_HOLDING_REGISTER | 1113 | 1 |  | u8 | 0 | 1 | 0
El. price, fixed, smart energy source | MODBUS_HOLDING_REGISTER | 1114 | 1 |  | u16 | 0 | 10000 | 100
El. price, smart energy source | MODBUS_HOLDING_REGISTER | 1115 | 1 |  | u8 | 0 | 1 | 0
El. price, fixed, smart energy source | MODBUS_HOLDING_REGISTER | 1116 | 1 |  | u16 | 0 | 10000 | 100
Prim. factor, smart energy source | MODBUS_HOLDING_REGISTER | 1117 | 10 |  | u8 | 0 | 50 | 25
Prim. factor, shunt add. heat smart energy source | MODBUS_HOLDING_REGISTER | 1118 | 10 |  | u8 | 0 | 50 | 10
Prim. factor, ext. step add. heat smart energy source | MODBUS_HOLDING_REGISTER | 1119 | 10 |  | u8 | 0 | 50 | 10
Prim. factor, OPT10 smart energy source | MODBUS_HOLDING_REGISTER | 1120 | 10 |  | u8 | 0 | 50 | 10
OPT10, high tariff price smart energy source | MODBUS_HOLDING_REGISTER | 1121 | 1 |  | u16 | 1 | 10000 | 100
OPT10, low tariff price smart energy source | MODBUS_HOLDING_REGISTER | 1122 | 1 |  | u16 | 1 | 10000 | 100
ext. step add. heat, high tariff price smart energy source | MODBUS_HOLDING_REGISTER | 1123 | 1 |  | u16 | 1 | 10000 | 100
ext. step add. heat, low tariff price smart energy source | MODBUS_HOLDING_REGISTER | 1124 | 1 |  | u16 | 1 | 10000 | 100
Shunt add. heat, high tariff price smart energy source | MODBUS_HOLDING_REGISTER | 1125 | 1 |  | u16 | 1 | 10000 | 100
Shunt add. heat, low tariff price smart energy source | MODBUS_HOLDING_REGISTER | 1126 | 1 |  | u16 | 1 | 10000 | 100
El. price, fixed, high tariff smart energy source | MODBUS_HOLDING_REGISTER | 1127 | 1 |  | u16 | 1 | 10000 | 100
El. price, fixed, low tariff smart energy source | MODBUS_HOLDING_REGISTER | 1128 | 1 |  | u16 | 1 | 10000 | 100
El. price, variable, high tariff smart energy source | MODBUS_HOLDING_REGISTER | 1129 | 1 |  | u16 | 1 | 10000 | 100
El. price, variable, low tariff smart energy source | MODBUS_HOLDING_REGISTER | 1130 | 1 |  | u16 | 1 | 10000 | 100
DM start source, priority 5 smart energy source | MODBUS_HOLDING_REGISTER | 1131 | 1 |  | s16 | 100 | 2000 | 400
DM start source, priority 4 smart energy source | MODBUS_HOLDING_REGISTER | 1132 | 1 |  | s16 | 100 | 2000 | 400
DM start source, priority 3 smart energy source | MODBUS_HOLDING_REGISTER | 1133 | 1 |  | s16 | 100 | 2000 | 400
DM start source, priority 2 smart energy source | MODBUS_HOLDING_REGISTER | 1134 | 1 |  | s16 | 100 | 2000 | 400
DM start source, priority 1 smart energy source | MODBUS_HOLDING_REGISTER | 1135 | 1 |  | s16 | -2000 | -10 | -60
Start day, tariff smart energy source | MODBUS_HOLDING_REGISTER | 1136 | 1 |  | u8 | 1 | 31 | 1
End day, tariff smart energy source | MODBUS_HOLDING_REGISTER | 1137 | 1 |  | u8 | 1 | 31 | 31
Start month, tariff smart energy source | MODBUS_HOLDING_REGISTER | 1138 | 1 |  | u8 | 1 | 12 | 1
End month, tariff smart energy source | MODBUS_HOLDING_REGISTER | 1139 | 1 |  | u8 | 1 | 12 | 12
Start day, fixed tariff smart energy source | MODBUS_HOLDING_REGISTER | 1172 | 1 |  | u8 | 1 | 31 | 1
End day, fixed tariff smart energy source | MODBUS_HOLDING_REGISTER | 1173 | 1 |  | u8 | 1 | 31 | 31
Start month, fixed tariff smart energy source | MODBUS_HOLDING_REGISTER | 1174 | 1 |  | u8 | 1 | 12 | 1
End month, fixed tariff smart energy source | MODBUS_HOLDING_REGISTER | 1175 | 1 |  | u8 | 1 | 12 | 12
Start day, tariff OPT10 smart energy source | MODBUS_HOLDING_REGISTER | 1208 | 1 |  | u8 | 1 | 31 | 1
End day, tariff OPT10 smart energy source | MODBUS_HOLDING_REGISTER | 1209 | 1 |  | u8 | 1 | 31 | 31
Start month, tariff OPT10 smart energy source | MODBUS_HOLDING_REGISTER | 1210 | 1 |  | u8 | 1 | 12 | 1
End month, tariff OPT10 smart energy source | MODBUS_HOLDING_REGISTER | 1211 | 1 |  | u8 | 1 | 12 | 12
Start day tariff, shunt additional heat smart energy source | MODBUS_HOLDING_REGISTER | 1244 | 1 |  | u8 | 1 | 31 | 1
End day tariff, shunt additional heat smart energy source | MODBUS_HOLDING_REGISTER | 1245 | 1 |  | u8 | 1 | 31 | 31
Start month tariff, shunt additional heat smart energy source | MODBUS_HOLDING_REGISTER | 1246 | 1 |  | u8 | 1 | 12 | 1
End month tariff, shunt additional heat smart energy source | MODBUS_HOLDING_REGISTER | 1247 | 1 |  | u8 | 1 | 12 | 12
Start day tariff, ext. step add. heat smart energy source | MODBUS_HOLDING_REGISTER | 1280 | 1 |  | u8 | 1 | 31 | 1
End day tariff, ext. step add. heat smart energy source | MODBUS_HOLDING_REGISTER | 1281 | 1 |  | u8 | 1 | 31 | 31
Start month tariff, ext. step add. heat smart energy source | MODBUS_HOLDING_REGISTER | 1282 | 1 |  | u8 | 1 | 12 | 1
End month tariff, ext. step add. heat smart energy source | MODBUS_HOLDING_REGISTER | 1283 | 1 |  | u8 | 1 | 12 | 12
Ground water pump temperature alarm | MODBUS_HOLDING_REGISTER | 1316 | 1 |  | u8 | 0 | 1 | 0
Ground water pump temperature alarm level | MODBUS_HOLDING_REGISTER | 1317 | 1 | °C | s8 | -15 | 20 | 3
Brine pump auto mode | MODBUS_HOLDING_REGISTER | 1319 | 1 |  | s8 | 0 | 2 | 1
Max difference, SES priority 1 energy source | MODBUS_HOLDING_REGISTER | 1326 | 10 | °C | s16 | 10 | 250 | 100
Max difference, SES lower priority energy source | MODBUS_HOLDING_REGISTER | 1327 | 10 | °C | s16 | 10 | 250 | 70
Installed (EB101) | MODBUS_HOLDING_REGISTER | 1550 | 1 |  | u8 | 0 | 1 | 1
EME20 | MODBUS_HOLDING_REGISTER | 4000 | 1 |  | u8 | 0 | 1 | 0
Current power | MODBUS_INPUT_REGISTER | 2176 | 1 | W | u32 | 0 | 0 | 0
Ground water pump's control signal | MODBUS_HOLDING_REGISTER | 4012 | 1 |  | s8 | 0 | 0 | 0
id:6028 | MODBUS_INPUT_REGISTER | 1993 | 1 |  | u8 | 0 | 0 | 0
id:6029 | MODBUS_INPUT_REGISTER | 1994 | 1 |  | u16 | 0 | 0 | 0
Total average power (Solar PV) | MODBUS_INPUT_REGISTER | 2178 | 100 | kW | u32 | 0 | 0 | 0
Total energy | MODBUS_INPUT_REGISTER | 2180 | 10 | kWh | s32 | 0 | 0 | 0
ERS 2 | MODBUS_HOLDING_REGISTER | 4076 | 1 |  | u8 | 0 | 1 | 0
ERS 3 | MODBUS_HOLDING_REGISTER | 4077 | 1 |  | u8 | 0 | 1 | 0
ERS 4 | MODBUS_HOLDING_REGISTER | 4078 | 1 |  | u8 | 0 | 1 | 0
id:6486 | MODBUS_HOLDING_REGISTER | 4135 | 1 |  | u8 | 0 | 1 | 0
id:6756 | MODBUS_INPUT_REGISTER | 2004 | 10 | %RH | s16 | 0 | 0 | 0
id:6757 | MODBUS_INPUT_REGISTER | 2005 | 10 | %RH | s16 | 0 | 0 | 0
id:6758 | MODBUS_INPUT_REGISTER | 2006 | 10 | %RH | s16 | 0 | 0 | 0
HTS 2 | MODBUS_HOLDING_REGISTER | 1981 | 1 |  | u8 | 0 | 1 | 0
HTS 3 | MODBUS_HOLDING_REGISTER | 1982 | 1 |  | u8 | 0 | 1 | 0
HTS 4 | MODBUS_HOLDING_REGISTER | 1983 | 1 |  | u8 | 0 | 1 | 0
External adjustment, cooling climate system 8 | MODBUS_HOLDING_REGISTER | 4138 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 7 | MODBUS_HOLDING_REGISTER | 4139 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 6 | MODBUS_HOLDING_REGISTER | 4140 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 5 | MODBUS_HOLDING_REGISTER | 4141 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 4 | MODBUS_HOLDING_REGISTER | 4142 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 3 | MODBUS_HOLDING_REGISTER | 4143 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 2 | MODBUS_HOLDING_REGISTER | 4144 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 1 | MODBUS_HOLDING_REGISTER | 4145 | 1 |  | s8 | -10 | 10 | 0
External adjustment with room sensor, cooling climate system 8 | MODBUS_HOLDING_REGISTER | 4146 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 7 | MODBUS_HOLDING_REGISTER | 4147 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 6 | MODBUS_HOLDING_REGISTER | 4148 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 5 | MODBUS_HOLDING_REGISTER | 4149 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 4 | MODBUS_HOLDING_REGISTER | 4150 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 3 | MODBUS_HOLDING_REGISTER | 4151 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 2 | MODBUS_HOLDING_REGISTER | 4152 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 1 | MODBUS_HOLDING_REGISTER | 4153 | 10 | °C | s16 | 50 | 300 | 200
id:6917 | MODBUS_HOLDING_REGISTER | 4072 | 1 |  | s16 | 0 | 200 | 1
id:6918 | MODBUS_HOLDING_REGISTER | 4073 | 1 |  | s16 | 0 | 20 | 1
id:6920 | MODBUS_HOLDING_REGISTER | 4074 | 1 |  | s16 | 0 | 20 | 0
id:6921 | MODBUS_HOLDING_REGISTER | 4075 | 1 |  | s16 | 1 | 100 | 15
id:6922 | MODBUS_HOLDING_REGISTER | 4154 | 10 |  | s16 | 0 | 200 | 30
id:6923 | MODBUS_HOLDING_REGISTER | 4155 | 1 |  | s16 | 0 | 20 | 2
blockFreq 1 (EB102) | MODBUS_HOLDING_REGISTER | 4164 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB103) | MODBUS_HOLDING_REGISTER | 4165 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB104) | MODBUS_HOLDING_REGISTER | 4166 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB105) | MODBUS_HOLDING_REGISTER | 4167 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB106) | MODBUS_HOLDING_REGISTER | 4168 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB107) | MODBUS_HOLDING_REGISTER | 4169 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB108) | MODBUS_HOLDING_REGISTER | 4170 | 1 |  | u8 | 0 | 1 | 0
id:6977 | MODBUS_HOLDING_REGISTER | 4201 | 1 |  | u8 | 0 | 100 | 0
Power at DOT, manual value | MODBUS_HOLDING_REGISTER | 4200 | 1 |  | u8 | 0 | 1 | 0
Blocking actions (ERS 3) | MODBUS_HOLDING_REGISTER | 4100 | 1 |  | u8 | 0 | 2 | 2
Blocking actions (ERS 4) | MODBUS_HOLDING_REGISTER | 4101 | 1 |  | u8 | 0 | 2 | 2
id:7048 | MODBUS_HOLDING_REGISTER | 5227 | 1 |  | u8 | 0 | 1 | 0
id:7122 | MODBUS_INPUT_REGISTER | 2401 | 10 | V | s8 | 0 | 0 | 0
id:7123 | MODBUS_INPUT_REGISTER | 2402 | 10 | V | s8 | 0 | 0 | 0
id:7124 | MODBUS_INPUT_REGISTER | 2403 | 10 | V | s8 | 0 | 0 | 0
id:7125 | MODBUS_INPUT_REGISTER | 2404 | 10 | V | s8 | 0 | 0 | 0
id:7126 | MODBUS_INPUT_REGISTER | 2405 | 10 | V | s8 | 0 | 0 | 0
id:7127 | MODBUS_INPUT_REGISTER | 2406 | 10 | V | s8 | 0 | 0 | 0
id:7128 | MODBUS_INPUT_REGISTER | 2407 | 10 | V | s8 | 0 | 0 | 0
id:7138 | MODBUS_HOLDING_REGISTER | 5441 | 1 | % | u8 | 0 | 100 | 70
id:7139 | MODBUS_HOLDING_REGISTER | 5442 | 1 |  | u8 | 0 | 1 | 0
id:7140 | MODBUS_HOLDING_REGISTER | 5443 | 1 |  | u8 | 0 | 1 | 0
id:7141 | MODBUS_HOLDING_REGISTER | 5444 | 1 | % | u8 | 0 | 100 | 70
id:7142 | MODBUS_HOLDING_REGISTER | 5445 | 1 |  | u8 | 0 | 1 | 0
id:7143 | MODBUS_HOLDING_REGISTER | 5446 | 1 |  | u8 | 0 | 1 | 0
id:7144 | MODBUS_HOLDING_REGISTER | 5447 | 1 | % | u8 | 0 | 100 | 70
id:7145 | MODBUS_HOLDING_REGISTER | 5448 | 1 |  | u8 | 0 | 1 | 0
id:7146 | MODBUS_HOLDING_REGISTER | 5449 | 1 |  | u8 | 0 | 1 | 0
id:7147 | MODBUS_HOLDING_REGISTER | 5450 | 1 | % | u8 | 0 | 100 | 70
id:7148 | MODBUS_HOLDING_REGISTER | 5451 | 1 |  | u8 | 0 | 1 | 0
id:7149 | MODBUS_HOLDING_REGISTER | 5452 | 1 |  | u8 | 0 | 1 | 0
id:7150 | MODBUS_HOLDING_REGISTER | 5453 | 1 | % | u8 | 0 | 100 | 70
id:7176 | MODBUS_HOLDING_REGISTER | 5455 | 1 |  | u8 | 0 | 1 | 0
id:7943 | MODBUS_INPUT_REGISTER | 2399 | 10 | % | u16 | 0 | 0 | 0
id:7944 | MODBUS_INPUT_REGISTER | 2400 | 10 | % | u16 | 0 | 0 | 0
id:8002 | MODBUS_HOLDING_REGISTER | 1996 | 1 | % | s8 | -15 | 10 | -3
id:8003 | MODBUS_HOLDING_REGISTER | 1997 | 1 | % | u8 | 1 | 254 | 65
Minimum permitted speed (EB101 GP12) | MODBUS_HOLDING_REGISTER | 5352 | 1 | % | u8 | 1 | 50 | 1
Start fan de-icing (EB101) | MODBUS_HOLDING_REGISTER | 5360 | 1 |  | s8 | 0 | 1 | 0
Defrost Requested EB101 | MODBUS_HOLDING_REGISTER | 5368 | 1 |  | s8 | 0 | 1 | 0
System 1 (RMU) | MODBUS_HOLDING_REGISTER | 176 | 1 |  | u8 | 0 | 1 | 0
System 2 (RMU) | MODBUS_HOLDING_REGISTER | 177 | 1 |  | u8 | 0 | 1 | 0
System 3 (RMU) | MODBUS_HOLDING_REGISTER | 178 | 1 |  | u8 | 0 | 1 | 0
System 4 (RMU) | MODBUS_HOLDING_REGISTER | 179 | 1 |  | u8 | 0 | 1 | 0
System 4 (RMU) | MODBUS_HOLDING_REGISTER | 1998 | 1 |  | u8 | 0 | 1 | 0
System 4 (RMU) | MODBUS_HOLDING_REGISTER | 1999 | 1 |  | u8 | 0 | 1 | 0
System 4 (RMU) | MODBUS_HOLDING_REGISTER | 2000 | 1 |  | u8 | 0 | 1 | 0
System 4 (RMU) | MODBUS_HOLDING_REGISTER | 2001 | 1 |  | u8 | 0 | 1 | 0
id:8302 | MODBUS_HOLDING_REGISTER | 5388 | 1 |  | u8 | 0 | 0 | 0
id:8982 | MODBUS_HOLDING_REGISTER | 5390 | 1 |  | u8 | 0 | 0 | 0
The start guide has been run | MODBUS_HOLDING_REGISTER | 2742 | 1 |  | u8 | 0 | 1 | 1
Audio signal on alarm | MODBUS_HOLDING_REGISTER | 5326 | 1 |  | u8 | 0 | 1 | 1
Sound when pressing button | MODBUS_HOLDING_REGISTER | 5327 | 1 |  | u8 | 0 | 1 | 1
BT12 offset, heat pump 1 | MODBUS_HOLDING_REGISTER | 5328 | 10 | °C | s8 | -50 | 50 | 0
Additional heat step, emergency mode | MODBUS_HOLDING_REGISTER | 3058 | 1 |  | u8 | 0 | 7 | 0
Heating, auto | MODBUS_HOLDING_REGISTER | 3059 | 1 |  | u8 | 0 | 1 | 1
Factor | MODBUS_HOLDING_REGISTER | 3033 | 1 |  | u8 | 1 | 10 | 5
id:10881 | MODBUS_HOLDING_REGISTER | 3062 | 1 |  | u8 | 0 | 1 | 0
id:10890 | MODBUS_HOLDING_REGISTER | 3063 | 1 |  | u8 | 0 | 1 | 0
id:12332 | MODBUS_HOLDING_REGISTER | 2767 | 1 |  | s16 | -32768 | 32767 | -32768
id:12333 | MODBUS_HOLDING_REGISTER | 2768 | 1 |  | s16 | -32768 | 32767 | -32768
id:12334 | MODBUS_HOLDING_REGISTER | 2769 | 1 |  | s16 | -32768 | 32767 | -32768
id:12335 | MODBUS_HOLDING_REGISTER | 2770 | 1 |  | s16 | -32768 | 32767 | -32768
id:12336 | MODBUS_HOLDING_REGISTER | 2771 | 1 |  | s16 | -32768 | 32767 | -32768
id:12337 | MODBUS_HOLDING_REGISTER | 2772 | 1 |  | s16 | -32768 | 32767 | -32768
id:12338 | MODBUS_HOLDING_REGISTER | 2773 | 1 |  | s16 | -32768 | 32767 | -32768
id:12339 | MODBUS_HOLDING_REGISTER | 2774 | 1 |  | s16 | -32768 | 32767 | -32768
id:12340 | MODBUS_HOLDING_REGISTER | 2775 | 1 |  | s16 | -32768 | 32767 | -32768
id:12341 | MODBUS_HOLDING_REGISTER | 2776 | 1 |  | s16 | -32768 | 32767 | -32768
id:12342 | MODBUS_HOLDING_REGISTER | 2777 | 1 |  | s16 | -32768 | 32767 | -32768
id:12343 | MODBUS_HOLDING_REGISTER | 2778 | 1 |  | s16 | -32768 | 32767 | -32768
id:12344 | MODBUS_HOLDING_REGISTER | 2779 | 1 |  | s16 | -32768 | 32767 | -32768
id:12345 | MODBUS_HOLDING_REGISTER | 2780 | 1 |  | s16 | -32768 | 32767 | -32768
id:12346 | MODBUS_HOLDING_REGISTER | 2781 | 1 |  | s16 | -32768 | 32767 | -32768
id:12347 | MODBUS_HOLDING_REGISTER | 2782 | 1 |  | s16 | -32768 | 32767 | -32768
id:12348 | MODBUS_HOLDING_REGISTER | 2783 | 1 |  | s16 | -32768 | 32767 | -32768
id:12349 | MODBUS_HOLDING_REGISTER | 2784 | 1 |  | s16 | -32768 | 32767 | -32768
id:12350 | MODBUS_HOLDING_REGISTER | 2785 | 1 |  | s16 | -32768 | 32767 | -32768
id:12351 | MODBUS_HOLDING_REGISTER | 2786 | 1 |  | s16 | -32768 | 32767 | -32768
id:12352 | MODBUS_HOLDING_REGISTER | 2787 | 1 |  | s16 | -32768 | 32767 | -32768
id:12353 | MODBUS_HOLDING_REGISTER | 2788 | 1 |  | s16 | -32768 | 32767 | -32768
id:12354 | MODBUS_HOLDING_REGISTER | 2789 | 1 |  | s16 | -32768 | 32767 | -32768
id:12355 | MODBUS_HOLDING_REGISTER | 2790 | 1 |  | s16 | -32768 | 32767 | -32768
id:12356 | MODBUS_HOLDING_REGISTER | 2791 | 1 |  | s16 | -32768 | 32767 | -32768
id:12357 | MODBUS_HOLDING_REGISTER | 2792 | 1 |  | s16 | -32768 | 32767 | -32768
id:12358 | MODBUS_HOLDING_REGISTER | 2793 | 1 |  | s16 | -32768 | 32767 | -32768
id:12359 | MODBUS_HOLDING_REGISTER | 2794 | 1 |  | s16 | -32768 | 32767 | -32768
id:12360 | MODBUS_HOLDING_REGISTER | 2795 | 1 |  | s16 | -32768 | 32767 | -32768
id:12361 | MODBUS_HOLDING_REGISTER | 2796 | 1 |  | s16 | -32768 | 32767 | -32768
id:12362 | MODBUS_HOLDING_REGISTER | 2797 | 1 |  | s16 | -32768 | 32767 | -32768
id:12363 | MODBUS_HOLDING_REGISTER | 2798 | 1 |  | s16 | -32768 | 32767 | -32768
id:12364 | MODBUS_HOLDING_REGISTER | 2799 | 1 |  | s16 | -32768 | 32767 | -32768
id:12365 | MODBUS_HOLDING_REGISTER | 2800 | 1 |  | s16 | -32768 | 32767 | -32768
id:12366 | MODBUS_HOLDING_REGISTER | 2801 | 1 |  | s16 | -32768 | 32767 | -32768
id:12367 | MODBUS_HOLDING_REGISTER | 2802 | 1 |  | s16 | -32768 | 32767 | -32768
id:12368 | MODBUS_HOLDING_REGISTER | 2803 | 1 |  | s16 | -32768 | 32767 | -32768
id:12369 | MODBUS_HOLDING_REGISTER | 2804 | 1 |  | s16 | -32768 | 32767 | -32768
id:12370 | MODBUS_HOLDING_REGISTER | 2805 | 1 |  | s16 | -32768 | 32767 | -32768
id:12371 | MODBUS_HOLDING_REGISTER | 2806 | 1 |  | s16 | -32768 | 32767 | -32768
id:12372 | MODBUS_HOLDING_REGISTER | 2807 | 1 |  | s16 | -32768 | 32767 | -32768
id:12373 | MODBUS_HOLDING_REGISTER | 2808 | 1 |  | s16 | -32768 | 32767 | -32768
id:12374 | MODBUS_HOLDING_REGISTER | 2809 | 1 |  | s16 | -32768 | 32767 | -32768
id:12375 | MODBUS_HOLDING_REGISTER | 2810 | 1 |  | s16 | -32768 | 32767 | -32768
id:12376 | MODBUS_HOLDING_REGISTER | 2811 | 1 |  | s16 | -32768 | 32767 | -32768
id:12377 | MODBUS_HOLDING_REGISTER | 2812 | 1 |  | s16 | -32768 | 32767 | -32768
id:12378 | MODBUS_HOLDING_REGISTER | 2813 | 1 |  | s16 | -32768 | 32767 | -32768
id:12379 | MODBUS_HOLDING_REGISTER | 2814 | 1 |  | s16 | -32768 | 32767 | -32768
id:12380 | MODBUS_HOLDING_REGISTER | 2815 | 1 |  | s16 | -32768 | 32767 | -32768
id:12381 | MODBUS_HOLDING_REGISTER | 2816 | 1 |  | s16 | -32768 | 32767 | -32768
id:12382 | MODBUS_HOLDING_REGISTER | 2817 | 1 |  | s16 | -32768 | 32767 | -32768
id:12383 | MODBUS_HOLDING_REGISTER | 2818 | 1 |  | s16 | -32768 | 32767 | -32768
id:12384 | MODBUS_HOLDING_REGISTER | 2819 | 1 |  | s16 | -32768 | 32767 | -32768
Period | MODBUS_HOLDING_REGISTER | 3088 | 1 |  | u8 | 0 | 1 | 0
Number of years | MODBUS_HOLDING_REGISTER | 3089 | 1 |  | u8 | 1 | 10 | 1
Months | MODBUS_HOLDING_REGISTER | 3090 | 1 |  | u32 | 0 | 4095 | 4095
Show outdoor temperature | MODBUS_HOLDING_REGISTER | 3096 | 1 |  | u8 | 0 | 0 | 0
Show indoor temperature | MODBUS_HOLDING_REGISTER | 3097 | 1 |  | u8 | 0 | 0 | 0
Active days | MODBUS_HOLDING_REGISTER | 3066 | 1 |  | u8 | 0 | 127 | 0
Active days | MODBUS_HOLDING_REGISTER | 3067 | 1 |  | u8 | 0 | 127 | 0
Active days | MODBUS_HOLDING_REGISTER | 3068 | 1 |  | u8 | 0 | 127 | 0
Active days | MODBUS_HOLDING_REGISTER | 3069 | 1 |  | u8 | 0 | 127 | 0
Active days | MODBUS_HOLDING_REGISTER | 3070 | 1 |  | u8 | 0 | 127 | 0
Start time | MODBUS_HOLDING_REGISTER | 5393 | 1 |  | -
Start time | MODBUS_HOLDING_REGISTER | 5397 | 1 |  | -
Stop time | MODBUS_HOLDING_REGISTER | 5401 | 1 |  | -
AUX relay (AUX11) | MODBUS_HOLDING_REGISTER | 224 | 1 |  | u8 | 0 | 30 | 5
id:12650 | MODBUS_HOLDING_REGISTER | 3104 | 1 |  | -
id:12651 | MODBUS_HOLDING_REGISTER | 3144 | 1 |  | -
id:12652 | MODBUS_HOLDING_REGISTER | 3184 | 1 |  | -
id:12653 | MODBUS_HOLDING_REGISTER | 3224 | 1 |  | -
id:12654 | MODBUS_HOLDING_REGISTER | 3264 | 1 |  | -
id:12655 | MODBUS_HOLDING_REGISTER | 3304 | 1 |  | -
id:12656 | MODBUS_HOLDING_REGISTER | 3344 | 1 |  | -
id:12657 | MODBUS_HOLDING_REGISTER | 3384 | 1 |  | -
id:12658 | MODBUS_HOLDING_REGISTER | 3424 | 1 |  | -
id:12659 | MODBUS_HOLDING_REGISTER | 3464 | 1 |  | -
id:12660 | MODBUS_HOLDING_REGISTER | 3504 | 1 |  | -
id:12661 | MODBUS_HOLDING_REGISTER | 3544 | 1 |  | -
id:12662 | MODBUS_HOLDING_REGISTER | 3584 | 1 |  | -
id:12663 | MODBUS_HOLDING_REGISTER | 3624 | 1 |  | -
id:12664 | MODBUS_HOLDING_REGISTER | 3664 | 1 |  | -
id:12665 | MODBUS_HOLDING_REGISTER | 3704 | 1 |  | -
id:12666 | MODBUS_HOLDING_REGISTER | 3744 | 1 |  | -
id:12667 | MODBUS_HOLDING_REGISTER | 3784 | 1 |  | -
id:12668 | MODBUS_HOLDING_REGISTER | 3824 | 1 |  | -
id:12669 | MODBUS_HOLDING_REGISTER | 3864 | 1 |  | -
id:12670 | MODBUS_HOLDING_REGISTER | 3904 | 1 |  | -
id:12671 | MODBUS_HOLDING_REGISTER | 2978 | 1 |  | u8 | 0 | 3 | 0
id:12672 | MODBUS_HOLDING_REGISTER | 2979 | 1 |  | u8 | 0 | 3 | 0
id:12673 | MODBUS_HOLDING_REGISTER | 2980 | 1 |  | u8 | 0 | 3 | 0
id:12674 | MODBUS_HOLDING_REGISTER | 2981 | 1 |  | u8 | 0 | 3 | 0
id:12675 | MODBUS_HOLDING_REGISTER | 2982 | 1 |  | u8 | 0 | 3 | 0
id:12676 | MODBUS_HOLDING_REGISTER | 2983 | 1 |  | u8 | 0 | 3 | 0
id:12677 | MODBUS_HOLDING_REGISTER | 2984 | 1 |  | u8 | 0 | 3 | 0
id:12678 | MODBUS_HOLDING_REGISTER | 2985 | 1 |  | u8 | 0 | 3 | 0
id:12679 | MODBUS_HOLDING_REGISTER | 2986 | 1 |  | u8 | 0 | 15 | 0
id:12680 | MODBUS_HOLDING_REGISTER | 2987 | 1 |  | u8 | 0 | 15 | 0
id:12681 | MODBUS_HOLDING_REGISTER | 2988 | 1 |  | u8 | 0 | 15 | 0
id:12682 | MODBUS_HOLDING_REGISTER | 2989 | 1 |  | u8 | 0 | 15 | 0
id:12683 | MODBUS_HOLDING_REGISTER | 2990 | 1 |  | u8 | 0 | 15 | 0
id:12684 | MODBUS_HOLDING_REGISTER | 2991 | 1 |  | u8 | 0 | 15 | 0
id:12685 | MODBUS_HOLDING_REGISTER | 2992 | 1 |  | u8 | 0 | 15 | 0
id:12686 | MODBUS_HOLDING_REGISTER | 2993 | 1 |  | u8 | 0 | 15 | 0
id:12687 | MODBUS_HOLDING_REGISTER | 2994 | 1 |  | u8 | 0 | 15 | 0
id:12688 | MODBUS_HOLDING_REGISTER | 2995 | 1 |  | u8 | 0 | 15 | 0
id:12689 | MODBUS_HOLDING_REGISTER | 2996 | 1 |  | u8 | 0 | 15 | 0
id:12690 | MODBUS_HOLDING_REGISTER | 2997 | 1 |  | u8 | 0 | 15 | 0
id:12691 | MODBUS_HOLDING_REGISTER | 2998 | 1 |  | u8 | 0 | 3 | 0
id:12692 | MODBUS_HOLDING_REGISTER | 3944 | 1 |  | u32 | 0 | 0 | 0
id:12693 | MODBUS_HOLDING_REGISTER | 3946 | 1 |  | u32 | 0 | 0 | 0
id:12694 | MODBUS_HOLDING_REGISTER | 3948 | 1 |  | u32 | 0 | 0 | 0
id:12695 | MODBUS_HOLDING_REGISTER | 3950 | 1 |  | u32 | 0 | 0 | 0
id:12696 | MODBUS_HOLDING_REGISTER | 3952 | 1 |  | u32 | 0 | 0 | 0
id:12697 | MODBUS_HOLDING_REGISTER | 3954 | 1 |  | u32 | 0 | 0 | 0
id:12698 | MODBUS_HOLDING_REGISTER | 3956 | 1 |  | u32 | 0 | 0 | 0
id:12699 | MODBUS_HOLDING_REGISTER | 3958 | 1 |  | u32 | 0 | 0 | 0
id:12700 | MODBUS_HOLDING_REGISTER | 3960 | 1 |  | u32 | 0 | 0 | 0
id:12701 | MODBUS_HOLDING_REGISTER | 3962 | 1 |  | u32 | 0 | 0 | 0
id:12702 | MODBUS_HOLDING_REGISTER | 3964 | 1 |  | u32 | 0 | 0 | 0
id:12703 | MODBUS_HOLDING_REGISTER | 3966 | 1 |  | u32 | 0 | 0 | 0
id:12704 | MODBUS_HOLDING_REGISTER | 3968 | 1 |  | u32 | 0 | 0 | 0
id:12705 | MODBUS_HOLDING_REGISTER | 3970 | 1 |  | u32 | 0 | 0 | 0
id:12706 | MODBUS_HOLDING_REGISTER | 3972 | 1 |  | u32 | 0 | 0 | 0
id:12707 | MODBUS_HOLDING_REGISTER | 3974 | 1 |  | u32 | 0 | 0 | 0
id:12708 | MODBUS_HOLDING_REGISTER | 3976 | 1 |  | u32 | 0 | 0 | 0
id:12709 | MODBUS_HOLDING_REGISTER | 3978 | 1 |  | u32 | 0 | 0 | 0
id:12710 | MODBUS_HOLDING_REGISTER | 3980 | 1 |  | u32 | 0 | 0 | 0
id:12711 | MODBUS_HOLDING_REGISTER | 3982 | 1 |  | u32 | 0 | 0 | 0
id:12712 | MODBUS_HOLDING_REGISTER | 3984 | 1 |  | u32 | 0 | 0 | 0
id:12801 | MODBUS_HOLDING_REGISTER | 2505 | 10 | °C | s32 | 50 | 350 | 200
id:12802 | MODBUS_HOLDING_REGISTER | 2507 | 10 | °C | s32 | 50 | 350 | 200
id:12803 | MODBUS_HOLDING_REGISTER | 2509 | 10 | °C | s32 | 50 | 350 | 200
id:12804 | MODBUS_HOLDING_REGISTER | 2511 | 10 | °C | s32 | 50 | 350 | 200
id:12805 | MODBUS_HOLDING_REGISTER | 2513 | 10 | °C | s32 | 50 | 350 | 200
id:12806 | MODBUS_HOLDING_REGISTER | 2515 | 10 | °C | s32 | 50 | 350 | 200
id:12807 | MODBUS_HOLDING_REGISTER | 2517 | 10 | °C | s32 | 50 | 350 | 200
id:12808 | MODBUS_HOLDING_REGISTER | 2519 | 10 | °C | s32 | 50 | 350 | 200
id:12809 | MODBUS_HOLDING_REGISTER | 2521 | 10 | °C | s32 | 50 | 350 | 200
id:12810 | MODBUS_HOLDING_REGISTER | 2523 | 10 | °C | s32 | 50 | 350 | 200
id:12811 | MODBUS_HOLDING_REGISTER | 2525 | 10 | °C | s32 | 50 | 350 | 200
id:12812 | MODBUS_HOLDING_REGISTER | 2527 | 10 | °C | s32 | 50 | 350 | 200
id:12813 | MODBUS_HOLDING_REGISTER | 2529 | 10 | °C | s32 | 50 | 350 | 200
id:12814 | MODBUS_HOLDING_REGISTER | 2531 | 10 | °C | s32 | 50 | 350 | 200
id:12815 | MODBUS_HOLDING_REGISTER | 2533 | 10 | °C | s32 | 50 | 350 | 200
id:12816 | MODBUS_HOLDING_REGISTER | 2535 | 10 | °C | s32 | 50 | 350 | 200
id:12817 | MODBUS_HOLDING_REGISTER | 2537 | 10 | °C | s32 | 50 | 350 | 200
id:12818 | MODBUS_HOLDING_REGISTER | 2539 | 10 | °C | s32 | 50 | 350 | 200
id:12819 | MODBUS_HOLDING_REGISTER | 2541 | 10 | °C | s32 | 50 | 350 | 200
id:12820 | MODBUS_HOLDING_REGISTER | 2543 | 10 | °C | s32 | 50 | 350 | 200
id:12821 | MODBUS_HOLDING_REGISTER | 2545 | 10 | °C | s32 | 50 | 350 | 200
id:12822 | MODBUS_HOLDING_REGISTER | 2547 | 10 | °C | s32 | 50 | 350 | 200
id:12823 | MODBUS_HOLDING_REGISTER | 2549 | 10 | °C | s32 | 50 | 350 | 200
id:12824 | MODBUS_HOLDING_REGISTER | 2551 | 10 | °C | s32 | 50 | 350 | 200
id:12825 | MODBUS_HOLDING_REGISTER | 2553 | 10 | °C | s32 | 50 | 350 | 200
id:12826 | MODBUS_HOLDING_REGISTER | 2555 | 10 | °C | s32 | 50 | 350 | 200
id:12827 | MODBUS_HOLDING_REGISTER | 2557 | 10 | °C | s32 | 50 | 350 | 200
id:12828 | MODBUS_HOLDING_REGISTER | 2559 | 10 | °C | s32 | 50 | 350 | 200
id:12829 | MODBUS_HOLDING_REGISTER | 2561 | 10 | °C | s32 | 50 | 350 | 200
id:12830 | MODBUS_HOLDING_REGISTER | 2563 | 10 | °C | s32 | 50 | 350 | 200
id:12831 | MODBUS_HOLDING_REGISTER | 2565 | 10 | °C | s32 | 50 | 350 | 200
id:12832 | MODBUS_HOLDING_REGISTER | 2567 | 10 | °C | s32 | 50 | 350 | 200
id:12833 | MODBUS_HOLDING_REGISTER | 2569 | 10 | °C | s32 | 50 | 350 | 200
id:12834 | MODBUS_HOLDING_REGISTER | 2571 | 10 | °C | s32 | 50 | 350 | 200
id:12835 | MODBUS_HOLDING_REGISTER | 2573 | 10 | °C | s32 | 50 | 350 | 200
id:12836 | MODBUS_HOLDING_REGISTER | 2575 | 10 | °C | s32 | 50 | 350 | 200
id:12837 | MODBUS_HOLDING_REGISTER | 2577 | 10 | °C | s32 | 50 | 350 | 200
id:12838 | MODBUS_HOLDING_REGISTER | 2579 | 10 | °C | s32 | 50 | 350 | 200
id:12839 | MODBUS_HOLDING_REGISTER | 2581 | 10 | °C | s32 | 50 | 350 | 200
id:12840 | MODBUS_HOLDING_REGISTER | 2583 | 10 | °C | s32 | 50 | 350 | 200
id:12841 | MODBUS_HOLDING_REGISTER | 2585 | 10 | °C | s32 | 50 | 350 | 250
id:12842 | MODBUS_HOLDING_REGISTER | 2587 | 10 | °C | s32 | 50 | 350 | 250
id:12843 | MODBUS_HOLDING_REGISTER | 2589 | 10 | °C | s32 | 50 | 350 | 250
id:12844 | MODBUS_HOLDING_REGISTER | 2591 | 10 | °C | s32 | 50 | 350 | 250
id:12845 | MODBUS_HOLDING_REGISTER | 2593 | 10 | °C | s32 | 50 | 350 | 250
id:12846 | MODBUS_HOLDING_REGISTER | 2595 | 10 | °C | s32 | 50 | 350 | 250
id:12847 | MODBUS_HOLDING_REGISTER | 2597 | 10 | °C | s32 | 50 | 350 | 250
id:12848 | MODBUS_HOLDING_REGISTER | 2599 | 10 | °C | s32 | 50 | 350 | 250
id:12849 | MODBUS_HOLDING_REGISTER | 2601 | 10 | °C | s32 | 50 | 350 | 250
id:12850 | MODBUS_HOLDING_REGISTER | 2603 | 10 | °C | s32 | 50 | 350 | 250
id:12851 | MODBUS_HOLDING_REGISTER | 2605 | 10 | °C | s32 | 50 | 350 | 250
id:12852 | MODBUS_HOLDING_REGISTER | 2607 | 10 | °C | s32 | 50 | 350 | 250
id:12853 | MODBUS_HOLDING_REGISTER | 2609 | 10 | °C | s32 | 50 | 350 | 250
id:12854 | MODBUS_HOLDING_REGISTER | 2611 | 10 | °C | s32 | 50 | 350 | 250
id:12855 | MODBUS_HOLDING_REGISTER | 2613 | 10 | °C | s32 | 50 | 350 | 250
id:12856 | MODBUS_HOLDING_REGISTER | 2615 | 10 | °C | s32 | 50 | 350 | 250
id:12857 | MODBUS_HOLDING_REGISTER | 2617 | 10 | °C | s32 | 50 | 350 | 250
id:12858 | MODBUS_HOLDING_REGISTER | 2619 | 10 | °C | s32 | 50 | 350 | 250
id:12859 | MODBUS_HOLDING_REGISTER | 2621 | 10 | °C | s32 | 50 | 350 | 250
id:12860 | MODBUS_HOLDING_REGISTER | 2623 | 10 | °C | s32 | 50 | 350 | 250
id:12861 | MODBUS_HOLDING_REGISTER | 2625 | 10 | °C | s32 | 50 | 350 | 250
id:12862 | MODBUS_HOLDING_REGISTER | 2627 | 10 | °C | s32 | 50 | 350 | 250
id:12863 | MODBUS_HOLDING_REGISTER | 2629 | 10 | °C | s32 | 50 | 350 | 250
id:12864 | MODBUS_HOLDING_REGISTER | 2631 | 10 | °C | s32 | 50 | 350 | 250
id:12865 | MODBUS_HOLDING_REGISTER | 2633 | 10 | °C | s32 | 50 | 350 | 250
id:12866 | MODBUS_HOLDING_REGISTER | 2635 | 10 | °C | s32 | 50 | 350 | 250
id:12867 | MODBUS_HOLDING_REGISTER | 2637 | 10 | °C | s32 | 50 | 350 | 250
id:12868 | MODBUS_HOLDING_REGISTER | 2639 | 10 | °C | s32 | 50 | 350 | 250
id:12869 | MODBUS_HOLDING_REGISTER | 2641 | 10 | °C | s32 | 50 | 350 | 250
id:12870 | MODBUS_HOLDING_REGISTER | 2643 | 10 | °C | s32 | 50 | 350 | 250
id:12871 | MODBUS_HOLDING_REGISTER | 2645 | 10 | °C | s32 | 50 | 350 | 250
id:12872 | MODBUS_HOLDING_REGISTER | 2647 | 10 | °C | s32 | 50 | 350 | 250
id:12873 | MODBUS_HOLDING_REGISTER | 2649 | 10 | °C | s32 | 50 | 350 | 250
id:12874 | MODBUS_HOLDING_REGISTER | 2651 | 10 | °C | s32 | 50 | 350 | 250
id:12875 | MODBUS_HOLDING_REGISTER | 2653 | 10 | °C | s32 | 50 | 350 | 250
id:12876 | MODBUS_HOLDING_REGISTER | 2655 | 10 | °C | s32 | 50 | 350 | 250
id:12877 | MODBUS_HOLDING_REGISTER | 2657 | 10 | °C | s32 | 50 | 350 | 250
id:12878 | MODBUS_HOLDING_REGISTER | 2659 | 10 | °C | s32 | 50 | 350 | 250
id:12879 | MODBUS_HOLDING_REGISTER | 2661 | 10 | °C | s32 | 50 | 350 | 250
id:12880 | MODBUS_HOLDING_REGISTER | 2663 | 10 | °C | s32 | 50 | 350 | 250
id:13655 | MODBUS_INPUT_REGISTER | 2411 | 1 |  | u8 | 0 | 0 | 0
id:13656 | MODBUS_INPUT_REGISTER | 2412 | 1 |  | u8 | 0 | 0 | 0
id:13796 | MODBUS_INPUT_REGISTER | 2243 | 1 |  | u8 | 0 | 0 | 0
id:13797 | MODBUS_INPUT_REGISTER | 2244 | 1 |  | u8 | 0 | 0 | 0
id:13798 | MODBUS_INPUT_REGISTER | 2245 | 1 |  | u8 | 0 | 0 | 0
id:13799 | MODBUS_INPUT_REGISTER | 2246 | 1 |  | u8 | 0 | 0 | 0
id:13800 | MODBUS_INPUT_REGISTER | 2247 | 1 |  | u8 | 0 | 0 | 0
id:13801 | MODBUS_INPUT_REGISTER | 2248 | 1 |  | u8 | 0 | 0 | 0
id:13802 | MODBUS_INPUT_REGISTER | 2249 | 1 |  | u8 | 0 | 0 | 0
id:13803 | MODBUS_INPUT_REGISTER | 2250 | 1 |  | u8 | 0 | 0 | 0
Offset cooling (Solar PV) | MODBUS_HOLDING_REGISTER | 2667 | 1 |  | s8 | -10 | 0 | -1
Offset heating (Solar PV) | MODBUS_HOLDING_REGISTER | 2668 | 1 |  | u8 | 0 | 10 | 1
Offset pool (Solar PV) | MODBUS_HOLDING_REGISTER | 2669 | 1 | °C | u8 | 0 | 10 | 10
Cooling (Solar PV) | MODBUS_HOLDING_REGISTER | 2666 | 1 |  | u8 | 0 | 1 | 0
AUX (Solar PV) | MODBUS_HOLDING_REGISTER | 2675 | 1 |  | u8 | 0 | 1 | 0
id:14052 | MODBUS_HOLDING_REGISTER | 2670 | 1 | kW | u32 | 1 | 999 | 1
id:14061 | MODBUS_HOLDING_REGISTER | 2672 | 1 |  | u8 | 0 | 1 | 0
Temperature, Overload, pool | MODBUS_HOLDING_REGISTER | 0 | 1 | °C | u8 | 1 | 50 | 1
Modbus TCP/IP Ext. (Solar PV) | MODBUS_HOLDING_REGISTER | 2107 | 1 |  | u8 | 0 | 1 | 0
Modbus TCP/IP Ext.Include own consumption (Solar PV) | MODBUS_HOLDING_REGISTER | 2108 | 1 |  | u8 | 0 | 1 | 0
Modbus TCP/IP Ext. Available power (Solar PV) | MODBUS_HOLDING_REGISTER | 2109 | 1 |  | u16 | 0 | 65535 | 0
External adjustment input, main unit (ECS1) | MODBUS_HOLDING_REGISTER | 2111 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS2) | MODBUS_HOLDING_REGISTER | 2112 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS3) | MODBUS_HOLDING_REGISTER | 2113 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS4) | MODBUS_HOLDING_REGISTER | 2114 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS5) | MODBUS_HOLDING_REGISTER | 2115 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS6) | MODBUS_HOLDING_REGISTER | 2116 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS7) | MODBUS_HOLDING_REGISTER | 2117 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS8) | MODBUS_HOLDING_REGISTER | 2118 | 1 |  | u8 | 0 | 1 | 0
Zone 1 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2119 | 1 |  | u8 | 0 | 1 | 0
Zone 2 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2120 | 1 |  | u8 | 0 | 1 | 0
Zone 3 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2121 | 1 |  | u8 | 0 | 1 | 0
Zone 4 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2122 | 1 |  | u8 | 0 | 1 | 0
Zone 5 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2123 | 1 |  | u8 | 0 | 1 | 0
Zone 6 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2124 | 1 |  | u8 | 0 | 1 | 0
Zone 7 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2125 | 1 |  | u8 | 0 | 1 | 0
Zone 8 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2126 | 1 |  | u8 | 0 | 1 | 0
Zone 9 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2127 | 1 |  | u8 | 0 | 1 | 0
Zone 10 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2128 | 1 |  | u8 | 0 | 1 | 0
Zone 11 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2129 | 1 |  | u8 | 0 | 1 | 0
Zone 12 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2130 | 1 |  | u8 | 0 | 1 | 0
Zone 13 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2131 | 1 |  | u8 | 0 | 1 | 0
Zone 14 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2132 | 1 |  | u8 | 0 | 1 | 0
Zone 15 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2133 | 1 |  | u8 | 0 | 1 | 0
Zone 16 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2134 | 1 |  | u8 | 0 | 1 | 0
Zone 17 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2135 | 1 |  | u8 | 0 | 1 | 0
Zone 18 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2136 | 1 |  | u8 | 0 | 1 | 0
Zone 19 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2137 | 1 |  | u8 | 0 | 1 | 0
Zone 20 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2138 | 1 |  | u8 | 0 | 1 | 0
Zone 21 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2139 | 1 |  | u8 | 0 | 1 | 0
Zone 22 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2140 | 1 |  | u8 | 0 | 1 | 0
Zone 23 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2141 | 1 |  | u8 | 0 | 1 | 0
Zone 24 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2142 | 1 |  | u8 | 0 | 1 | 0
Zone 25 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2143 | 1 |  | u8 | 0 | 1 | 0
Zone 26 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2144 | 1 |  | u8 | 0 | 1 | 0
Zone 27 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2145 | 1 |  | u8 | 0 | 1 | 0
Zone 28 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2146 | 1 |  | u8 | 0 | 1 | 0
Zone 29 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2147 | 1 |  | u8 | 0 | 1 | 0
Zone 30 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2148 | 1 |  | u8 | 0 | 1 | 0
Zone 31 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2149 | 1 |  | u8 | 0 | 1 | 0
Zone 32 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2150 | 1 |  | u8 | 0 | 1 | 0
Zone 33 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2151 | 1 |  | u8 | 0 | 1 | 0
Zone 34 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2152 | 1 |  | u8 | 0 | 1 | 0
Zone 35 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2153 | 1 |  | u8 | 0 | 1 | 0
Zone 36 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2154 | 1 |  | u8 | 0 | 1 | 0
Zone 37 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2155 | 1 |  | u8 | 0 | 1 | 0
Zone 38 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2156 | 1 |  | u8 | 0 | 1 | 0
Zone 39 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2157 | 1 |  | u8 | 0 | 1 | 0
Zone 40 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2158 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS1 | MODBUS_HOLDING_REGISTER | 2439 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS2 | MODBUS_HOLDING_REGISTER | 2440 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS3 | MODBUS_HOLDING_REGISTER | 2441 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS4 | MODBUS_HOLDING_REGISTER | 2442 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS5 | MODBUS_HOLDING_REGISTER | 2443 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS6 | MODBUS_HOLDING_REGISTER | 2444 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS7 | MODBUS_HOLDING_REGISTER | 2445 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS8 | MODBUS_HOLDING_REGISTER | 2446 | 1 |  | u8 | 0 | 1 | 0
External setting for adjustment migrated | MODBUS_HOLDING_REGISTER | 2503 | 1 |  | u8 | 0 | 1 | 0
Max. step internal additional heat | MODBUS_HOLDING_REGISTER | 2504 | 1 |  | u8 | 0 | 7 | 3
Version, inverter (EB101) | MODBUS_INPUT_REGISTER | 2147 | 1 |  | u8 | 0 | 0 | 0
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2676 | 1 |  | u8 | 1 | 24 | 3
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2677 | 1 |  | u8 | 1 | 24 | 3
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2678 | 1 |  | u8 | 1 | 24 | 3
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2679 | 1 |  | u8 | 1 | 24 | 3
Total oper. time ext. add. heat, heating | MODBUS_INPUT_REGISTER | 2182 | 10 | h | s32 | 0 | 9999999 | 0
Total HW run time additional heat | MODBUS_INPUT_REGISTER | 2184 | 10 | h | s32 | 0 | 9999999 | 0
id:21077 | MODBUS_HOLDING_REGISTER | 3020 | 1 |  | u8 | 0 | 0 | 0
id:21078 | MODBUS_HOLDING_REGISTER | 3021 | 1 |  | u8 | 0 | 0 | 0
id:21079 | MODBUS_HOLDING_REGISTER | 3022 | 1 |  | u8 | 0 | 0 | 0
id:21080 | MODBUS_HOLDING_REGISTER | 3023 | 1 |  | u8 | 0 | 0 | 0
id:21081 | MODBUS_HOLDING_REGISTER | 3024 | 1 |  | u8 | 0 | 0 | 0
id:21082 | MODBUS_HOLDING_REGISTER | 3025 | 1 |  | u8 | 0 | 0 | 0
id:21083 | MODBUS_HOLDING_REGISTER | 3026 | 1 |  | u8 | 0 | 0 | 0
id:21084 | MODBUS_HOLDING_REGISTER | 3027 | 1 |  | u8 | 0 | 0 | 0
id:21189 | MODBUS_INPUT_REGISTER | 2726 | 1 |  | u16 | 0 | 0 | 0
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2700 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2701 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2702 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2703 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2704 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2705 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2706 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2707 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2708 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2709 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2710 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2711 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2712 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2713 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2714 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2715 | 1 | h | u8 | 1 | 24 | 4
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2728 | 1 |  | u8 | 1 | 24 | 3
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2729 | 1 |  | u8 | 1 | 24 | 3
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2730 | 1 |  | u8 | 1 | 24 | 3
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2731 | 1 |  | u8 | 1 | 24 | 3
AUX from Modbus | MODBUS_HOLDING_REGISTER | 2740 | 1 |  | u8 | 0 | 68 | 0
AUX from Modbus | MODBUS_HOLDING_REGISTER | 2741 | 1 |  | s16 | 0 | 0 | 0
Heat pump test - Silent mode (EB101/EB102) | MODBUS_HOLDING_REGISTER | 5101 | 1 |  | u8 | 0 | 1 | 0
Last defrost, heat pump 1 | MODBUS_INPUT_REGISTER | 2158 | 1 |  | u8 | 0 | 255 | 255
ERS 2 | MODBUS_HOLDING_REGISTER | 2820 | 1 |  | u8 | 0 | 1 | 0
ERS 3 | MODBUS_HOLDING_REGISTER | 2821 | 1 |  | u8 | 0 | 1 | 0
ERS 4 | MODBUS_HOLDING_REGISTER | 2822 | 1 |  | u8 | 0 | 1 | 0
ERS 4 | MODBUS_HOLDING_REGISTER | 2823 | 1 |  | u8 | 0 | 1 | 0
ERS 4 | MODBUS_HOLDING_REGISTER | 2824 | 1 |  | u8 | 0 | 1 | 1
ERS 4 | MODBUS_HOLDING_REGISTER | 2825 | 1 |  | u8 | 0 | 1 | 1
ERS 4 | MODBUS_HOLDING_REGISTER | 2826 | 1 |  | u8 | 0 | 1 | 1
ERS 4 | MODBUS_HOLDING_REGISTER | 2827 | 1 |  | u8 | 0 | 1 | 1
Min. vent temp. (ERS 4) | MODBUS_HOLDING_REGISTER | 2857 | 1 | °C | u8 | 0 | 10 | 3
Min. vent temp. (ERS 4) | MODBUS_HOLDING_REGISTER | 2858 | 1 | °C | u8 | 0 | 10 | 3
Min. vent temp. (ERS 4) | MODBUS_HOLDING_REGISTER | 2859 | 1 | °C | u8 | 0 | 10 | 3
Min. vent temp. (ERS 4) | MODBUS_HOLDING_REGISTER | 2860 | 1 | °C | u8 | 0 | 10 | 3
Blocking actions (ERS 4) | MODBUS_HOLDING_REGISTER | 2828 | 1 |  | u8 | 0 | 2 | 2
Blocking actions (ERS 4) | MODBUS_HOLDING_REGISTER | 2829 | 1 |  | u8 | 0 | 2 | 2
Blocking actions (ERS 4) | MODBUS_HOLDING_REGISTER | 2830 | 1 |  | u8 | 0 | 2 | 2
Blocking actions (ERS 4) | MODBUS_HOLDING_REGISTER | 2831 | 1 |  | u8 | 0 | 2 | 2
id:23145 | MODBUS_HOLDING_REGISTER | 2921 | 1 |  | u8 | 0 | 1 | 0
id:23146 | MODBUS_HOLDING_REGISTER | 2922 | 1 |  | u8 | 0 | 1 | 0
id:23147 | MODBUS_HOLDING_REGISTER | 2923 | 1 |  | u8 | 0 | 1 | 0
id:23148 | MODBUS_HOLDING_REGISTER | 2924 | 1 |  | u8 | 0 | 1 | 0
id:23149 | MODBUS_HOLDING_REGISTER | 2836 | 10 | °C | s16 | -200 | 410 | 190
id:23150 | MODBUS_HOLDING_REGISTER | 2837 | 10 | °C | s16 | -200 | 410 | 190
id:23151 | MODBUS_HOLDING_REGISTER | 2838 | 10 | °C | s16 | -200 | 410 | 190
id:23152 | MODBUS_HOLDING_REGISTER | 2839 | 10 | °C | s16 | -200 | 410 | 190
id:23153 | MODBUS_HOLDING_REGISTER | 2832 | 10 | °C | s16 | 30 | 100 | 30
id:23154 | MODBUS_HOLDING_REGISTER | 2833 | 10 | °C | s16 | 30 | 100 | 30
id:23155 | MODBUS_HOLDING_REGISTER | 2834 | 10 | °C | s16 | 30 | 100 | 30
id:23156 | MODBUS_HOLDING_REGISTER | 2835 | 10 | °C | s16 | 30 | 100 | 30
Fan mode 5 | MODBUS_INPUT_REGISTER | 2168 | 1 | % | u8 | 0 | 0 | 0
Fan mode 6 | MODBUS_INPUT_REGISTER | 2169 | 1 | % | u8 | 0 | 0 | 0
Fan mode 7 | MODBUS_INPUT_REGISTER | 2170 | 1 | % | u8 | 0 | 0 | 0
Fan mode 8 | MODBUS_INPUT_REGISTER | 2171 | 1 | % | u8 | 0 | 0 | 0
Disable emergency restart GP1 | MODBUS_HOLDING_REGISTER | 5392 | 1 |  | u8 | 0 | 1 | 0
Disable emergency restart GP1 | MODBUS_HOLDING_REGISTER | 5025 | 1 |  | u8 | 0 | 1 | 0
Modbus external control | MODBUS_HOLDING_REGISTER | 5008 | 1 |  | u8 | 0 | 1 | 0
id:24484 | MODBUS_HOLDING_REGISTER | 5009 | 10 | °C | s16 | 50 | 800 | 450
id:24485 | MODBUS_HOLDING_REGISTER | 5010 | 10 | °C | s16 | 50 | 800 | 450
id:24486 | MODBUS_HOLDING_REGISTER | 5011 | 10 | °C | s16 | 50 | 800 | 450
id:24487 | MODBUS_HOLDING_REGISTER | 5012 | 10 | °C | s16 | 50 | 800 | 450
id:24488 | MODBUS_HOLDING_REGISTER | 5013 | 10 | °C | s16 | 50 | 800 | 450
id:24489 | MODBUS_HOLDING_REGISTER | 5014 | 10 | °C | s16 | 50 | 800 | 450
id:24490 | MODBUS_HOLDING_REGISTER | 5015 | 10 | °C | s16 | 50 | 800 | 450
id:24491 | MODBUS_HOLDING_REGISTER | 5016 | 10 | °C | s16 | 50 | 800 | 450
id:24492 | MODBUS_HOLDING_REGISTER | 5017 | 10 | °C | s16 | -50 | 300 | 250
id:24493 | MODBUS_HOLDING_REGISTER | 5018 | 10 | °C | s16 | -50 | 300 | 250
id:24494 | MODBUS_HOLDING_REGISTER | 5019 | 10 | °C | s16 | -50 | 300 | 250
id:24495 | MODBUS_HOLDING_REGISTER | 5020 | 10 | °C | s16 | -50 | 300 | 250
id:24496 | MODBUS_HOLDING_REGISTER | 5021 | 10 | °C | s16 | -50 | 300 | 250
id:24497 | MODBUS_HOLDING_REGISTER | 5022 | 10 | °C | s16 | -50 | 300 | 250
id:24498 | MODBUS_HOLDING_REGISTER | 5023 | 10 | °C | s16 | -50 | 300 | 250
id:24499 | MODBUS_HOLDING_REGISTER | 5024 | 10 | °C | s16 | -50 | 300 | 250
id:24681 | MODBUS_HOLDING_REGISTER | 5056 | 1 |  | u8 | 0 | 1 | 0
id:24682 | MODBUS_HOLDING_REGISTER | 5057 | 1 |  | u8 | 0 | 1 | 0
id:24683 | MODBUS_HOLDING_REGISTER | 5058 | 1 |  | u8 | 0 | 255 | 0
id:24684 | MODBUS_HOLDING_REGISTER | 5059 | 1 |  | u8 | 0 | 1 | 0
Relay status | MODBUS_INPUT_REGISTER | 0 | 1 |  | u8 | 0 | 0 | 0
id:24969 | MODBUS_HOLDING_REGISTER | 5060 | 1 |  | u8 | 0 | 1 | 0
id:24970 | MODBUS_HOLDING_REGISTER | 5061 | 1 |  | s16 | -100 | 10000 | 0
id:24971 | MODBUS_HOLDING_REGISTER | 5062 | 1 |  | u8 | 0 | 1 | 0
id:24972 | MODBUS_HOLDING_REGISTER | 5063 | 1 |  | u16 | 0 | 1000 | 0
id:24973 | MODBUS_HOLDING_REGISTER | 5064 | 1 |  | u8 | 0 | 1 | 0
id:24974 | MODBUS_HOLDING_REGISTER | 5065 | 1 |  | u8 | 0 | 1 | 0
id:24975 | MODBUS_HOLDING_REGISTER | 5066 | 1 |  | u16 | 0 | 1000 | 0
id:24976 | MODBUS_HOLDING_REGISTER | 5067 | 1 |  | u8 | 0 | 1 | 0
id:24977 | MODBUS_HOLDING_REGISTER | 5068 | 1 |  | u8 | 0 | 1 | 0
id:24978 | MODBUS_HOLDING_REGISTER | 5069 | 1 |  | u16 | 0 | 1000 | 0
id:24979 | MODBUS_HOLDING_REGISTER | 5070 | 1 |  | u8 | 0 | 1 | 0
id:24980 | MODBUS_HOLDING_REGISTER | 5071 | 1 |  | u16 | 0 | 1000 | 0
Energy log - Produced energy for heating over the past hour | MODBUS_INPUT_REGISTER | 2283 | 100 | kWh | u32 | 0 | 0 | 0
Energy log - Used energy for heating over the past hour | MODBUS_INPUT_REGISTER | 2291 | 100 | kWh | u32 | 0 | 0 | 0
Energy log - Used energy by additional heater for heating over the past hour | MODBUS_INPUT_REGISTER | 2299 | 100 | kWh | u32 | 0 | 0 | 0
Energy log - Current power consumption | MODBUS_INPUT_REGISTER | 2305 | 100 | kWh | u32 | 0 | 0 | 0
Energy log - Current power consumption, components | MODBUS_INPUT_REGISTER | 2408 | 100 | kWh | u32 | 0 | 0 | 0
Compressor, total time energy storage, main unit (EP14) | MODBUS_INPUT_REGISTER | 2335 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, main unit (EP15) | MODBUS_INPUT_REGISTER | 2337 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 1 (EP14) | MODBUS_INPUT_REGISTER | 2339 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 1 (EP15) | MODBUS_INPUT_REGISTER | 2341 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 2 (EP14) | MODBUS_INPUT_REGISTER | 2343 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 2 (EP15) | MODBUS_INPUT_REGISTER | 2345 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 3 (EP14) | MODBUS_INPUT_REGISTER | 2347 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 3 (EP15) | MODBUS_INPUT_REGISTER | 2349 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 4 (EP14) | MODBUS_INPUT_REGISTER | 2351 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 4 (EP15) | MODBUS_INPUT_REGISTER | 2353 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 5 (EP14) | MODBUS_INPUT_REGISTER | 2355 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 5 (EP15) | MODBUS_INPUT_REGISTER | 2357 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 6 (EP14) | MODBUS_INPUT_REGISTER | 2359 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 6 (EP15) | MODBUS_INPUT_REGISTER | 2361 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 7 (EP14) | MODBUS_INPUT_REGISTER | 2363 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 7 (EP15) | MODBUS_INPUT_REGISTER | 2365 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 8 (EP14) | MODBUS_INPUT_REGISTER | 2367 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 8 (EP15) | MODBUS_INPUT_REGISTER | 2369 | 1 | h | u32 | 0 | 2147483647 | 0
id:26694 | MODBUS_HOLDING_REGISTER | 5208 | 1 |  | u8 | 0 | 1 | 0
id:26695 | MODBUS_HOLDING_REGISTER | 5209 | 1 |  | u8 | 0 | 1 | 0
id:26696 | MODBUS_HOLDING_REGISTER | 5210 | 1 |  | u8 | 0 | 1 | 0
id:26697 | MODBUS_HOLDING_REGISTER | 5211 | 1 |  | u8 | 0 | 1 | 0
id:26698 | MODBUS_HOLDING_REGISTER | 5212 | 1 |  | u8 | 0 | 1 | 0
id:26699 | MODBUS_HOLDING_REGISTER | 5213 | 1 |  | u8 | 0 | 1 | 0
id:26702 | MODBUS_HOLDING_REGISTER | 5216 | 1 |  | u8 | 0 | 1 | 0
id:26703 | MODBUS_HOLDING_REGISTER | 5217 | 10 | °C | s16 | 0 | 0 | 0
id:26704 | MODBUS_HOLDING_REGISTER | 5218 | 10 | °C | s16 | 0 | 0 | 0
id:26705 | MODBUS_HOLDING_REGISTER | 5219 | 10 | °C | s16 | 0 | 0 | 0
id:26706 | MODBUS_HOLDING_REGISTER | 5220 | 10 | °C | s16 | 0 | 0 | 0
id:26707 | MODBUS_HOLDING_REGISTER | 5221 | 10 | °C | s16 | 0 | 0 | 0
id:26708 | MODBUS_HOLDING_REGISTER | 5222 | 10 | °C | s16 | 0 | 0 | 0
id:26711 | MODBUS_HOLDING_REGISTER | 5225 | 10 | °C | s16 | 0 | 0 | 0
id:26793 | MODBUS_INPUT_REGISTER | 2375 | 1 |  | u8 | 0 | 7 | 7
id:26794 | MODBUS_INPUT_REGISTER | 2376 | 1 |  | u8 | 0 | 7 | 7
id:26795 | MODBUS_INPUT_REGISTER | 2377 | 1 |  | u8 | 0 | 7 | 7
id:26796 | MODBUS_INPUT_REGISTER | 2378 | 1 |  | u8 | 0 | 7 | 7
id:26797 | MODBUS_INPUT_REGISTER | 2379 | 1 |  | u8 | 0 | 7 | 7
id:26798 | MODBUS_INPUT_REGISTER | 2380 | 1 |  | u8 | 0 | 7 | 7
id:26799 | MODBUS_INPUT_REGISTER | 2381 | 1 |  | u8 | 0 | 7 | 7
id:26800 | MODBUS_INPUT_REGISTER | 2382 | 1 |  | u8 | 0 | 7 | 7
id:26801 | MODBUS_INPUT_REGISTER | 2383 | 1 |  | u8 | 0 | 7 | 7
id:26802 | MODBUS_INPUT_REGISTER | 2384 | 1 |  | u8 | 0 | 7 | 7
id:26803 | MODBUS_INPUT_REGISTER | 2385 | 1 |  | u8 | 0 | 7 | 7
id:26804 | MODBUS_INPUT_REGISTER | 2386 | 1 |  | u8 | 0 | 7 | 7
id:26805 | MODBUS_INPUT_REGISTER | 2387 | 1 |  | u8 | 0 | 7 | 7
id:26806 | MODBUS_INPUT_REGISTER | 2388 | 1 |  | u8 | 0 | 7 | 7
id:26807 | MODBUS_INPUT_REGISTER | 2389 | 1 |  | u8 | 0 | 7 | 7
id:26808 | MODBUS_INPUT_REGISTER | 2390 | 1 |  | u8 | 0 | 7 | 7
id:26809 | MODBUS_INPUT_REGISTER | 2391 | 1 |  | u8 | 0 | 7 | 7
id:26810 | MODBUS_INPUT_REGISTER | 2392 | 1 |  | u8 | 0 | 7 | 7
id:26811 | MODBUS_INPUT_REGISTER | 2393 | 1 |  | u8 | 0 | 7 | 7
id:26812 | MODBUS_INPUT_REGISTER | 2394 | 1 |  | u8 | 0 | 7 | 7
id:26813 | MODBUS_INPUT_REGISTER | 2395 | 1 |  | u8 | 0 | 7 | 7
id:26814 | MODBUS_INPUT_REGISTER | 2396 | 1 |  | u8 | 0 | 7 | 7
id:26815 | MODBUS_INPUT_REGISTER | 2397 | 1 |  | u8 | 0 | 7 | 7
id:26816 | MODBUS_INPUT_REGISTER | 2398 | 1 |  | u8 | 0 | 7 | 7
id:26817 | MODBUS_HOLDING_REGISTER | 5183 | 1 |  | s16 | -32768 | 32767 | 32767
id:26818 | MODBUS_HOLDING_REGISTER | 5184 | 1 |  | s16 | -32768 | 32767 | 32767
id:26819 | MODBUS_HOLDING_REGISTER | 5185 | 1 |  | s16 | -32768 | 32767 | 32767
id:26820 | MODBUS_HOLDING_REGISTER | 5186 | 1 |  | s16 | -32768 | 32767 | 32767
id:26821 | MODBUS_HOLDING_REGISTER | 5187 | 1 |  | s16 | -32768 | 32767 | 32767
id:26822 | MODBUS_HOLDING_REGISTER | 5188 | 1 |  | s16 | -32768 | 32767 | 32767
id:26823 | MODBUS_HOLDING_REGISTER | 5189 | 1 |  | s16 | -32768 | 32767 | 32767
id:26824 | MODBUS_HOLDING_REGISTER | 5190 | 1 |  | s16 | -32768 | 32767 | 32767
id:26825 | MODBUS_HOLDING_REGISTER | 5191 | 1 |  | s16 | -32768 | 32767 | 32767
id:26826 | MODBUS_HOLDING_REGISTER | 5192 | 1 |  | s16 | -32768 | 32767 | 32767
id:26827 | MODBUS_HOLDING_REGISTER | 5193 | 1 |  | s16 | -32768 | 32767 | 32767
id:26828 | MODBUS_HOLDING_REGISTER | 5194 | 1 |  | s16 | -32768 | 32767 | 32767
id:26829 | MODBUS_HOLDING_REGISTER | 5195 | 1 |  | s16 | -32768 | 32767 | 32767
id:26830 | MODBUS_HOLDING_REGISTER | 5196 | 1 |  | s16 | -32768 | 32767 | 32767
id:26831 | MODBUS_HOLDING_REGISTER | 5197 | 1 |  | s16 | -32768 | 32767 | 32767
id:26832 | MODBUS_HOLDING_REGISTER | 5198 | 1 |  | s16 | -32768 | 32767 | 32767
id:26833 | MODBUS_HOLDING_REGISTER | 5199 | 1 |  | s16 | -32768 | 32767 | 32767
id:26834 | MODBUS_HOLDING_REGISTER | 5200 | 1 |  | s16 | -32768 | 32767 | 32767
id:26835 | MODBUS_HOLDING_REGISTER | 5201 | 1 |  | s16 | -32768 | 32767 | 32767
id:26836 | MODBUS_HOLDING_REGISTER | 5202 | 1 |  | s16 | -32768 | 32767 | 32767
id:26837 | MODBUS_HOLDING_REGISTER | 5203 | 1 |  | s16 | -32768 | 32767 | 32767
id:26838 | MODBUS_HOLDING_REGISTER | 5204 | 1 |  | s16 | -32768 | 32767 | 32767
id:26839 | MODBUS_HOLDING_REGISTER | 5205 | 1 |  | s16 | -32768 | 32767 | 32767
id:26840 | MODBUS_HOLDING_REGISTER | 5206 | 1 |  | s16 | -32768 | 32767 | 32767
id:26865 | MODBUS_HOLDING_REGISTER | 5181 | 1 |  | u8 | 0 | 1 | 0
id:26867 | MODBUS_HOLDING_REGISTER | 5182 | 1 |  | u8 | 0 | 0 | 0
Heating, compressor only | MODBUS_INPUT_REGISTER | 1585 | 10 | kWh | u32 | 0 | 0 | 0
Hot water, including int. add. heat | MODBUS_INPUT_REGISTER | 1575 | 10 | kWh | u32 | 0 | 0 | 0
id:27790 | MODBUS_INPUT_REGISTER | 2437 | 1 |  | u8 | 0 | 0 | 0
id:27791 | MODBUS_INPUT_REGISTER | 2438 | 1 |  | u8 | 0 | 0 | 0
id:27792 | MODBUS_INPUT_REGISTER | 2439 | 1 |  | u8 | 0 | 0 | 0
id:27793 | MODBUS_INPUT_REGISTER | 2440 | 1 |  | u8 | 0 | 0 | 0
id:27794 | MODBUS_INPUT_REGISTER | 2441 | 1 |  | u8 | 0 | 0 | 0
id:27795 | MODBUS_INPUT_REGISTER | 2442 | 1 |  | u8 | 0 | 0 | 0
id:27796 | MODBUS_INPUT_REGISTER | 2443 | 1 |  | u8 | 0 | 0 | 0
id:27797 | MODBUS_INPUT_REGISTER | 2444 | 1 |  | u8 | 0 | 0 | 0
id:27814 | MODBUS_INPUT_REGISTER | 46 | 10 | A | u32 | 0 | 0 | 0
id:27815 | MODBUS_INPUT_REGISTER | 48 | 10 | A | u32 | 0 | 0 | 0
id:27816 | MODBUS_INPUT_REGISTER | 50 | 10 | A | u32 | 0 | 0 | 0
id:27818 | MODBUS_HOLDING_REGISTER | 5459 | 1 |  | u8 | 0 | 1 | 0
id:27819 | MODBUS_HOLDING_REGISTER | 5460 | 1 |  | u8 | 0 | 1 | 0
id:27854 | MODBUS_HOLDING_REGISTER | 5078 | 1 |  | u8 | 0 | 1 | 0
id:27855 | MODBUS_HOLDING_REGISTER | 5079 | 1 |  | u8 | 0 | 100 | 0
id:28034 | MODBUS_INPUT_REGISTER | 2445 | 10 | °C | s16 | 0 | 0 | 0
id:28035 | MODBUS_INPUT_REGISTER | 2446 | 10 | °C | s16 | 0 | 0 | 0
id:28036 | MODBUS_INPUT_REGISTER | 2447 | 10 | °C | s16 | 0 | 0 | 0
id:28037 | MODBUS_INPUT_REGISTER | 2448 | 10 | °C | s16 | 0 | 0 | 0
id:28038 | MODBUS_INPUT_REGISTER | 2449 | 10 | °C | s16 | 0 | 0 | 0
id:28039 | MODBUS_INPUT_REGISTER | 2450 | 10 | °C | s16 | 0 | 0 | 0
id:28040 | MODBUS_INPUT_REGISTER | 2451 | 10 | °C | s16 | 0 | 0 | 0
id:28041 | MODBUS_INPUT_REGISTER | 2452 | 10 | °C | s16 | 0 | 0 | 0
id:28042 | MODBUS_INPUT_REGISTER | 2453 | 10 | °C | s16 | 0 | 0 | 0
id:28200 | MODBUS_HOLDING_REGISTER | 5518 | 1 |  | u8 | 0 | 0 | 0
id:28201 | MODBUS_HOLDING_REGISTER | 5519 | 1 |  | u8 | 0 | 0 | 0
id:28202 | MODBUS_HOLDING_REGISTER | 5520 | 1 |  | u8 | 0 | 0 | 0
id:28203 | MODBUS_HOLDING_REGISTER | 5521 | 1 |  | u8 | 0 | 0 | 0
id:28204 | MODBUS_HOLDING_REGISTER | 5522 | 1 |  | u8 | 0 | 0 | 0
id:28205 | MODBUS_HOLDING_REGISTER | 5523 | 1 |  | u8 | 0 | 0 | 0
id:28206 | MODBUS_HOLDING_REGISTER | 5524 | 1 |  | u8 | 0 | 0 | 0
id:28207 | MODBUS_HOLDING_REGISTER | 5525 | 1 |  | u8 | 0 | 0 | 0
id:28208 | MODBUS_HOLDING_REGISTER | 5470 | 1 |  | u8 | 0 | 0 | 0
id:28209 | MODBUS_HOLDING_REGISTER | 5471 | 1 |  | u8 | 0 | 0 | 0
id:28210 | MODBUS_HOLDING_REGISTER | 5472 | 1 |  | u8 | 0 | 0 | 0
id:28211 | MODBUS_HOLDING_REGISTER | 5473 | 1 |  | u8 | 0 | 0 | 0
id:28212 | MODBUS_HOLDING_REGISTER | 5474 | 1 |  | u8 | 0 | 0 | 0
id:28213 | MODBUS_HOLDING_REGISTER | 5475 | 1 |  | u8 | 0 | 0 | 0
id:28214 | MODBUS_HOLDING_REGISTER | 5476 | 1 |  | u8 | 0 | 0 | 0
id:28215 | MODBUS_HOLDING_REGISTER | 5477 | 1 |  | u8 | 0 | 0 | 0
id:28216 | MODBUS_HOLDING_REGISTER | 5494 | 1 |  | u8 | 0 | 0 | 0
id:28217 | MODBUS_HOLDING_REGISTER | 5495 | 1 |  | u8 | 0 | 0 | 0
id:28218 | MODBUS_HOLDING_REGISTER | 5496 | 1 |  | u8 | 0 | 0 | 0
id:28219 | MODBUS_HOLDING_REGISTER | 5497 | 1 |  | u8 | 0 | 0 | 0
id:28220 | MODBUS_HOLDING_REGISTER | 5498 | 1 |  | u8 | 0 | 0 | 0
id:28221 | MODBUS_HOLDING_REGISTER | 5499 | 1 |  | u8 | 0 | 0 | 0
id:28222 | MODBUS_HOLDING_REGISTER | 5500 | 1 |  | u8 | 0 | 0 | 0
id:28223 | MODBUS_HOLDING_REGISTER | 5501 | 1 |  | u8 | 0 | 0 | 0
id:28224 | MODBUS_HOLDING_REGISTER | 5526 | 1 | Hz | u8 | 0 | 0 | 0
id:28225 | MODBUS_HOLDING_REGISTER | 5527 | 1 | Hz | u8 | 0 | 0 | 0
id:28226 | MODBUS_HOLDING_REGISTER | 5528 | 1 | Hz | u8 | 0 | 0 | 0
id:28227 | MODBUS_HOLDING_REGISTER | 5529 | 1 | Hz | u8 | 0 | 0 | 0
id:28228 | MODBUS_HOLDING_REGISTER | 5530 | 1 | Hz | u8 | 0 | 0 | 0
id:28229 | MODBUS_HOLDING_REGISTER | 5531 | 1 | Hz | u8 | 0 | 0 | 0
id:28230 | MODBUS_HOLDING_REGISTER | 5532 | 1 | Hz | u8 | 0 | 0 | 0
id:28231 | MODBUS_HOLDING_REGISTER | 5533 | 1 | Hz | u8 | 0 | 0 | 0
id:28232 | MODBUS_HOLDING_REGISTER | 5542 | 1 |  | u8 | 0 | 0 | 0
id:28233 | MODBUS_HOLDING_REGISTER | 5543 | 1 |  | u8 | 0 | 0 | 0
id:28234 | MODBUS_HOLDING_REGISTER | 5544 | 1 |  | u8 | 0 | 0 | 0
id:28235 | MODBUS_HOLDING_REGISTER | 5545 | 1 |  | u8 | 0 | 0 | 0
id:28236 | MODBUS_HOLDING_REGISTER | 5546 | 1 |  | u8 | 0 | 0 | 0
id:28237 | MODBUS_HOLDING_REGISTER | 5547 | 1 |  | u8 | 0 | 0 | 0
id:28238 | MODBUS_HOLDING_REGISTER | 5548 | 1 |  | u8 | 0 | 0 | 0
id:28239 | MODBUS_HOLDING_REGISTER | 5549 | 1 |  | u8 | 0 | 0 | 0
id:28240 | MODBUS_HOLDING_REGISTER | 5534 | 1 |  | u8 | 0 | 0 | 0
id:28241 | MODBUS_HOLDING_REGISTER | 5535 | 1 |  | u8 | 0 | 0 | 0
id:28242 | MODBUS_HOLDING_REGISTER | 5536 | 1 |  | u8 | 0 | 0 | 0
id:28243 | MODBUS_HOLDING_REGISTER | 5537 | 1 |  | u8 | 0 | 0 | 0
id:28244 | MODBUS_HOLDING_REGISTER | 5538 | 1 |  | u8 | 0 | 0 | 0
id:28245 | MODBUS_HOLDING_REGISTER | 5539 | 1 |  | u8 | 0 | 0 | 0
id:28246 | MODBUS_HOLDING_REGISTER | 5540 | 1 |  | u8 | 0 | 0 | 0
id:28247 | MODBUS_HOLDING_REGISTER | 5541 | 1 |  | u8 | 0 | 0 | 0
id:28248 | MODBUS_HOLDING_REGISTER | 5478 | 1 | % | u8 | 0 | 0 | 0
id:28249 | MODBUS_HOLDING_REGISTER | 5479 | 1 | % | u8 | 0 | 0 | 0
id:28250 | MODBUS_HOLDING_REGISTER | 5480 | 1 | % | u8 | 0 | 0 | 0
id:28251 | MODBUS_HOLDING_REGISTER | 5481 | 1 | % | u8 | 0 | 0 | 0
id:28252 | MODBUS_HOLDING_REGISTER | 5482 | 1 | % | u8 | 0 | 0 | 0
id:28253 | MODBUS_HOLDING_REGISTER | 5483 | 1 | % | u8 | 0 | 0 | 0
id:28254 | MODBUS_HOLDING_REGISTER | 5484 | 1 | % | u8 | 0 | 0 | 0
id:28255 | MODBUS_HOLDING_REGISTER | 5485 | 1 | % | u8 | 0 | 0 | 0
id:28256 | MODBUS_HOLDING_REGISTER | 5486 | 1 | % | u8 | 0 | 0 | 0
id:28257 | MODBUS_HOLDING_REGISTER | 5487 | 1 | % | u8 | 0 | 0 | 0
id:28258 | MODBUS_HOLDING_REGISTER | 5488 | 1 | % | u8 | 0 | 0 | 0
id:28259 | MODBUS_HOLDING_REGISTER | 5489 | 1 | % | u8 | 0 | 0 | 0
id:28260 | MODBUS_HOLDING_REGISTER | 5490 | 1 | % | u8 | 0 | 0 | 0
id:28261 | MODBUS_HOLDING_REGISTER | 5491 | 1 | % | u8 | 0 | 0 | 0
id:28262 | MODBUS_HOLDING_REGISTER | 5492 | 1 | % | u8 | 0 | 0 | 0
id:28263 | MODBUS_HOLDING_REGISTER | 5493 | 1 | % | u8 | 0 | 0 | 0
id:28264 | MODBUS_HOLDING_REGISTER | 5502 | 1 | % | u8 | 0 | 0 | 0
id:28265 | MODBUS_HOLDING_REGISTER | 5503 | 1 | % | u8 | 0 | 0 | 0
id:28266 | MODBUS_HOLDING_REGISTER | 5504 | 1 | % | u8 | 0 | 0 | 0
id:28267 | MODBUS_HOLDING_REGISTER | 5505 | 1 | % | u8 | 0 | 0 | 0
id:28268 | MODBUS_HOLDING_REGISTER | 5506 | 1 | % | u8 | 0 | 0 | 0
id:28269 | MODBUS_HOLDING_REGISTER | 5507 | 1 | % | u8 | 0 | 0 | 0
id:28270 | MODBUS_HOLDING_REGISTER | 5508 | 1 | % | u8 | 0 | 0 | 0
id:28271 | MODBUS_HOLDING_REGISTER | 5509 | 1 | % | u8 | 0 | 0 | 0
id:28272 | MODBUS_HOLDING_REGISTER | 5510 | 1 | % | u8 | 0 | 0 | 0
id:28273 | MODBUS_HOLDING_REGISTER | 5511 | 1 | % | u8 | 0 | 0 | 0
id:28274 | MODBUS_HOLDING_REGISTER | 5512 | 1 | % | u8 | 0 | 0 | 0
id:28275 | MODBUS_HOLDING_REGISTER | 5513 | 1 | % | u8 | 0 | 0 | 0
id:28276 | MODBUS_HOLDING_REGISTER | 5514 | 1 | % | u8 | 0 | 0 | 0
id:28277 | MODBUS_HOLDING_REGISTER | 5515 | 1 | % | u8 | 0 | 0 | 0
id:28278 | MODBUS_HOLDING_REGISTER | 5516 | 1 | % | u8 | 0 | 0 | 0
id:28279 | MODBUS_HOLDING_REGISTER | 5517 | 1 | % | u8 | 0 | 0 | 0
Boiler temperature (BT52) | MODBUS_INPUT_REGISTER | 3800 | 10 | °C | s16 | 0 | 0 | 0
id:28403 | MODBUS_HOLDING_REGISTER | 5600 | 1 |  | s32 | -10000 | 10000 | 100
id:28404 | MODBUS_HOLDING_REGISTER | 5602 | 1 |  | s32 | -10000 | 10000 | 100
id:28405 | MODBUS_HOLDING_REGISTER | 5604 | 1 |  | s32 | -10000 | 10000 | 100
id:28406 | MODBUS_HOLDING_REGISTER | 5606 | 1 |  | s32 | -10000 | 10000 | 100
id:28407 | MODBUS_HOLDING_REGISTER | 5608 | 1 |  | s32 | -10000 | 10000 | 100
id:28408 | MODBUS_HOLDING_REGISTER | 5610 | 1 |  | s32 | -10000 | 10000 | 100
id:28409 | MODBUS_HOLDING_REGISTER | 5612 | 1 |  | s32 | -10000 | 10000 | 100
id:28410 | MODBUS_HOLDING_REGISTER | 5614 | 1 |  | s32 | -10000 | 10000 | 100
id:28411 | MODBUS_HOLDING_REGISTER | 5616 | 1 |  | s32 | -10000 | 10000 | 100
id:28412 | MODBUS_HOLDING_REGISTER | 5618 | 1 |  | s32 | -10000 | 10000 | 100
id:28413 | MODBUS_HOLDING_REGISTER | 5620 | 1 |  | s32 | -10000 | 10000 | 100
id:28414 | MODBUS_HOLDING_REGISTER | 5622 | 1 |  | s32 | -10000 | 10000 | 100
id:28415 | MODBUS_HOLDING_REGISTER | 5624 | 1 |  | s32 | -10000 | 10000 | 100
id:28416 | MODBUS_HOLDING_REGISTER | 5626 | 1 |  | s32 | -10000 | 10000 | 100
id:28417 | MODBUS_HOLDING_REGISTER | 5628 | 1 |  | s32 | -10000 | 10000 | 100
id:28418 | MODBUS_HOLDING_REGISTER | 5630 | 1 |  | s32 | -10000 | 10000 | 100
id:28419 | MODBUS_HOLDING_REGISTER | 5632 | 1 |  | s32 | -10000 | 10000 | 100
id:28420 | MODBUS_HOLDING_REGISTER | 5634 | 1 |  | s32 | -10000 | 10000 | 100
id:28421 | MODBUS_HOLDING_REGISTER | 5636 | 1 |  | s32 | -10000 | 10000 | 100
id:28422 | MODBUS_HOLDING_REGISTER | 5638 | 1 |  | s32 | -10000 | 10000 | 100
id:28423 | MODBUS_HOLDING_REGISTER | 5640 | 1 |  | s32 | -10000 | 10000 | 100
id:28424 | MODBUS_HOLDING_REGISTER | 5642 | 1 |  | s32 | -10000 | 10000 | 100
id:28425 | MODBUS_HOLDING_REGISTER | 5644 | 1 |  | s32 | -10000 | 10000 | 100
id:28426 | MODBUS_HOLDING_REGISTER | 5646 | 1 |  | s32 | -10000 | 10000 | 100
id:28427 | MODBUS_HOLDING_REGISTER | 5648 | 1 |  | s32 | -10000 | 10000 | 100
id:28428 | MODBUS_HOLDING_REGISTER | 5650 | 1 |  | s32 | -10000 | 10000 | 100
id:28429 | MODBUS_HOLDING_REGISTER | 5652 | 1 |  | s32 | -10000 | 10000 | 100
id:28430 | MODBUS_HOLDING_REGISTER | 5654 | 1 |  | s32 | -10000 | 10000 | 100
id:28431 | MODBUS_HOLDING_REGISTER | 5656 | 1 |  | s32 | -10000 | 10000 | 100
id:28432 | MODBUS_HOLDING_REGISTER | 5658 | 1 |  | s32 | -10000 | 10000 | 100
id:28433 | MODBUS_HOLDING_REGISTER | 5660 | 1 |  | s32 | -10000 | 10000 | 100
id:28434 | MODBUS_HOLDING_REGISTER | 5662 | 1 |  | s32 | -10000 | 10000 | 100
id:28435 | MODBUS_HOLDING_REGISTER | 5664 | 1 |  | s32 | -10000 | 10000 | 100
id:28436 | MODBUS_HOLDING_REGISTER | 5666 | 1 |  | s32 | -10000 | 10000 | 100
id:28437 | MODBUS_HOLDING_REGISTER | 5668 | 1 |  | s32 | -10000 | 10000 | 100
id:28438 | MODBUS_HOLDING_REGISTER | 5670 | 1 |  | s32 | -10000 | 10000 | 100
id:28439 | MODBUS_HOLDING_REGISTER | 5672 | 1 |  | s32 | -10000 | 10000 | 100
id:28440 | MODBUS_HOLDING_REGISTER | 5674 | 1 |  | s32 | -10000 | 10000 | 100
id:28441 | MODBUS_HOLDING_REGISTER | 5676 | 1 |  | s32 | -10000 | 10000 | 100
id:28442 | MODBUS_HOLDING_REGISTER | 5678 | 1 |  | s32 | -10000 | 10000 | 100
id:28443 | MODBUS_HOLDING_REGISTER | 5680 | 1 |  | s32 | -10000 | 10000 | 100
id:28444 | MODBUS_HOLDING_REGISTER | 5682 | 1 |  | s32 | -10000 | 10000 | 100
id:28445 | MODBUS_HOLDING_REGISTER | 5684 | 1 |  | s32 | -10000 | 10000 | 100
id:28446 | MODBUS_HOLDING_REGISTER | 5686 | 1 |  | s32 | -10000 | 10000 | 100
id:28447 | MODBUS_HOLDING_REGISTER | 5688 | 1 |  | s32 | -10000 | 10000 | 100
id:28448 | MODBUS_HOLDING_REGISTER | 5690 | 1 |  | s32 | -10000 | 10000 | 100
id:28449 | MODBUS_HOLDING_REGISTER | 5692 | 1 |  | s32 | -10000 | 10000 | 100
id:28450 | MODBUS_HOLDING_REGISTER | 5694 | 1 |  | s32 | -10000 | 10000 | 100
id:28451 | MODBUS_HOLDING_REGISTER | 5696 | 1 |  | s32 | -10000 | 10000 | 100
id:28452 | MODBUS_HOLDING_REGISTER | 5698 | 1 |  | s32 | -10000 | 10000 | 100
id:28453 | MODBUS_HOLDING_REGISTER | 5700 | 1 |  | s32 | -10000 | 10000 | 100
id:28454 | MODBUS_HOLDING_REGISTER | 5702 | 1 |  | s32 | -10000 | 10000 | 100
id:28455 | MODBUS_HOLDING_REGISTER | 5704 | 1 |  | s32 | -10000 | 10000 | 100
id:28456 | MODBUS_HOLDING_REGISTER | 5706 | 1 |  | s32 | -10000 | 10000 | 100
id:28457 | MODBUS_HOLDING_REGISTER | 5708 | 1 |  | s32 | -10000 | 10000 | 100
id:28458 | MODBUS_HOLDING_REGISTER | 5710 | 1 |  | s32 | -10000 | 10000 | 100
id:28459 | MODBUS_HOLDING_REGISTER | 5712 | 1 |  | s32 | -10000 | 10000 | 100
id:28460 | MODBUS_HOLDING_REGISTER | 5714 | 1 |  | s32 | -10000 | 10000 | 100
id:28461 | MODBUS_HOLDING_REGISTER | 5716 | 1 |  | s32 | -10000 | 10000 | 100
id:28462 | MODBUS_HOLDING_REGISTER | 5718 | 1 |  | s32 | -10000 | 10000 | 100
id:28463 | MODBUS_HOLDING_REGISTER | 5720 | 1 |  | s32 | -10000 | 10000 | 100
id:28464 | MODBUS_HOLDING_REGISTER | 5722 | 1 |  | s32 | -10000 | 10000 | 100
id:28465 | MODBUS_HOLDING_REGISTER | 5724 | 1 |  | s32 | -10000 | 10000 | 100
id:28466 | MODBUS_HOLDING_REGISTER | 5726 | 1 |  | s32 | -10000 | 10000 | 100
id:28467 | MODBUS_HOLDING_REGISTER | 5728 | 1 |  | s32 | -10000 | 10000 | 100
id:28468 | MODBUS_HOLDING_REGISTER | 5730 | 1 |  | s32 | -10000 | 10000 | 100
id:28469 | MODBUS_HOLDING_REGISTER | 5732 | 1 |  | s32 | -10000 | 10000 | 100
id:28470 | MODBUS_HOLDING_REGISTER | 5734 | 1 |  | s32 | -10000 | 10000 | 100
id:28471 | MODBUS_HOLDING_REGISTER | 5736 | 1 |  | s32 | -10000 | 10000 | 100
id:28472 | MODBUS_HOLDING_REGISTER | 5738 | 1 |  | s32 | -10000 | 10000 | 100
id:28473 | MODBUS_HOLDING_REGISTER | 5740 | 1 |  | s32 | -10000 | 10000 | 100
id:28474 | MODBUS_HOLDING_REGISTER | 5742 | 1 |  | s32 | -10000 | 10000 | 100
id:28475 | MODBUS_HOLDING_REGISTER | 5744 | 1 |  | s32 | -10000 | 10000 | 100
id:28476 | MODBUS_HOLDING_REGISTER | 5746 | 1 |  | s32 | -10000 | 10000 | 100
id:28477 | MODBUS_HOLDING_REGISTER | 5748 | 1 |  | s32 | -10000 | 10000 | 100
id:28478 | MODBUS_HOLDING_REGISTER | 5750 | 1 |  | s32 | -10000 | 10000 | 100
id:28479 | MODBUS_HOLDING_REGISTER | 5752 | 1 |  | s32 | -10000 | 10000 | 100
id:28480 | MODBUS_HOLDING_REGISTER | 5754 | 1 |  | s32 | -10000 | 10000 | 100
id:28481 | MODBUS_HOLDING_REGISTER | 5756 | 1 |  | s32 | -10000 | 10000 | 100
id:28482 | MODBUS_HOLDING_REGISTER | 5758 | 1 |  | s32 | -10000 | 10000 | 100
id:28483 | MODBUS_HOLDING_REGISTER | 5760 | 1 |  | s32 | -10000 | 10000 | 100
id:28484 | MODBUS_HOLDING_REGISTER | 5762 | 1 |  | s32 | -10000 | 10000 | 100
id:28485 | MODBUS_HOLDING_REGISTER | 5764 | 1 |  | s32 | -10000 | 10000 | 100
id:28486 | MODBUS_HOLDING_REGISTER | 5766 | 1 |  | s32 | -10000 | 10000 | 100
id:28487 | MODBUS_HOLDING_REGISTER | 5768 | 1 |  | s32 | -10000 | 10000 | 100
id:28488 | MODBUS_HOLDING_REGISTER | 5770 | 1 |  | s32 | -10000 | 10000 | 100
id:28489 | MODBUS_HOLDING_REGISTER | 5772 | 1 |  | s32 | -10000 | 10000 | 100
id:28490 | MODBUS_HOLDING_REGISTER | 5774 | 1 |  | s32 | -10000 | 10000 | 100
id:28491 | MODBUS_HOLDING_REGISTER | 5776 | 1 |  | s32 | -10000 | 10000 | 100
id:28492 | MODBUS_HOLDING_REGISTER | 5778 | 1 |  | s32 | -10000 | 10000 | 100
id:28493 | MODBUS_HOLDING_REGISTER | 5780 | 1 |  | s32 | -10000 | 10000 | 100
id:28494 | MODBUS_HOLDING_REGISTER | 5782 | 1 |  | s32 | -10000 | 10000 | 100
id:28495 | MODBUS_HOLDING_REGISTER | 5784 | 1 |  | s32 | -10000 | 10000 | 100
id:28496 | MODBUS_HOLDING_REGISTER | 5786 | 1 |  | s32 | -10000 | 10000 | 100
id:28497 | MODBUS_HOLDING_REGISTER | 5788 | 1 |  | s32 | -10000 | 10000 | 100
id:28498 | MODBUS_HOLDING_REGISTER | 5790 | 1 |  | s32 | -10000 | 10000 | 100
id:28500 | MODBUS_HOLDING_REGISTER | 5792 | 1 |  | s32 | -10000 | 10000 | 100
id:28501 | MODBUS_HOLDING_REGISTER | 5794 | 1 |  | s32 | -10000 | 10000 | 100
id:28502 | MODBUS_HOLDING_REGISTER | 5796 | 1 |  | s32 | -10000 | 10000 | 100
id:28503 | MODBUS_HOLDING_REGISTER | 5798 | 1 |  | s32 | -10000 | 10000 | 100
id:28504 | MODBUS_HOLDING_REGISTER | 5800 | 1 |  | s32 | -10000 | 10000 | 100
id:28505 | MODBUS_HOLDING_REGISTER | 5802 | 1 |  | s32 | -10000 | 10000 | 100
id:28506 | MODBUS_HOLDING_REGISTER | 5804 | 1 |  | s32 | -10000 | 10000 | 100
id:28507 | MODBUS_HOLDING_REGISTER | 5806 | 1 |  | s32 | -10000 | 10000 | 100
id:28508 | MODBUS_HOLDING_REGISTER | 5808 | 1 |  | s32 | -10000 | 10000 | 100
id:28509 | MODBUS_HOLDING_REGISTER | 5810 | 1 |  | s32 | -10000 | 10000 | 100
id:28510 | MODBUS_HOLDING_REGISTER | 5812 | 1 |  | s32 | -10000 | 10000 | 100
id:28511 | MODBUS_HOLDING_REGISTER | 5814 | 1 |  | s32 | -10000 | 10000 | 100
id:28512 | MODBUS_HOLDING_REGISTER | 5816 | 1 |  | s32 | -10000 | 10000 | 100
id:28513 | MODBUS_HOLDING_REGISTER | 5818 | 1 |  | s32 | -10000 | 10000 | 100
id:28514 | MODBUS_HOLDING_REGISTER | 5820 | 1 |  | s32 | -10000 | 10000 | 100
id:28515 | MODBUS_HOLDING_REGISTER | 5822 | 1 |  | s32 | -10000 | 10000 | 100
id:28516 | MODBUS_HOLDING_REGISTER | 5824 | 1 |  | s32 | -10000 | 10000 | 100
id:28517 | MODBUS_HOLDING_REGISTER | 5826 | 1 |  | s32 | -10000 | 10000 | 100
id:28518 | MODBUS_HOLDING_REGISTER | 5828 | 1 |  | s32 | -10000 | 10000 | 100
id:28519 | MODBUS_HOLDING_REGISTER | 5830 | 1 |  | s32 | -10000 | 10000 | 100
id:28520 | MODBUS_HOLDING_REGISTER | 5832 | 1 |  | s32 | -10000 | 10000 | 100
id:28521 | MODBUS_HOLDING_REGISTER | 5834 | 1 |  | s32 | -10000 | 10000 | 100
id:28522 | MODBUS_HOLDING_REGISTER | 5836 | 1 |  | s32 | -10000 | 10000 | 100
id:28523 | MODBUS_HOLDING_REGISTER | 5838 | 1 |  | s32 | -10000 | 10000 | 100
id:28524 | MODBUS_HOLDING_REGISTER | 5840 | 1 |  | s32 | -10000 | 10000 | 100
id:28525 | MODBUS_HOLDING_REGISTER | 5842 | 1 |  | s32 | -10000 | 10000 | 100
id:28526 | MODBUS_HOLDING_REGISTER | 5844 | 1 |  | s32 | -10000 | 10000 | 100
id:28527 | MODBUS_HOLDING_REGISTER | 5846 | 1 |  | s32 | -10000 | 10000 | 100
id:28528 | MODBUS_HOLDING_REGISTER | 5848 | 1 |  | s32 | -10000 | 10000 | 100
id:28529 | MODBUS_HOLDING_REGISTER | 5850 | 1 |  | s32 | -10000 | 10000 | 100
id:28530 | MODBUS_HOLDING_REGISTER | 5852 | 1 |  | s32 | -10000 | 10000 | 100
id:28531 | MODBUS_HOLDING_REGISTER | 5854 | 1 |  | s32 | -10000 | 10000 | 100
id:28532 | MODBUS_HOLDING_REGISTER | 5856 | 1 |  | s32 | -10000 | 10000 | 100
id:28533 | MODBUS_HOLDING_REGISTER | 5858 | 1 |  | s32 | -10000 | 10000 | 100
id:28534 | MODBUS_HOLDING_REGISTER | 5860 | 1 |  | s32 | -10000 | 10000 | 100
id:28535 | MODBUS_HOLDING_REGISTER | 5862 | 1 |  | s32 | -10000 | 10000 | 100
id:28536 | MODBUS_HOLDING_REGISTER | 5864 | 1 |  | s32 | -10000 | 10000 | 100
id:28537 | MODBUS_HOLDING_REGISTER | 5866 | 1 |  | s32 | -10000 | 10000 | 100
id:28538 | MODBUS_HOLDING_REGISTER | 5868 | 1 |  | s32 | -10000 | 10000 | 100
id:28539 | MODBUS_HOLDING_REGISTER | 5870 | 1 |  | s32 | -10000 | 10000 | 100
id:28540 | MODBUS_HOLDING_REGISTER | 5872 | 1 |  | s32 | -10000 | 10000 | 100
id:28541 | MODBUS_HOLDING_REGISTER | 5874 | 1 |  | s32 | -10000 | 10000 | 100
id:28542 | MODBUS_HOLDING_REGISTER | 5876 | 1 |  | s32 | -10000 | 10000 | 100
id:28543 | MODBUS_HOLDING_REGISTER | 5878 | 1 |  | s32 | -10000 | 10000 | 100
id:28544 | MODBUS_HOLDING_REGISTER | 5880 | 1 |  | s32 | -10000 | 10000 | 100
id:28545 | MODBUS_HOLDING_REGISTER | 5882 | 1 |  | s32 | -10000 | 10000 | 100
id:28546 | MODBUS_HOLDING_REGISTER | 5884 | 1 |  | s32 | -10000 | 10000 | 100
id:28547 | MODBUS_HOLDING_REGISTER | 5886 | 1 |  | s32 | -10000 | 10000 | 100
id:28548 | MODBUS_HOLDING_REGISTER | 5888 | 1 |  | s32 | -10000 | 10000 | 100
id:28549 | MODBUS_HOLDING_REGISTER | 5890 | 1 |  | s32 | -10000 | 10000 | 100
id:28550 | MODBUS_HOLDING_REGISTER | 5892 | 1 |  | s32 | -10000 | 10000 | 100
id:28551 | MODBUS_HOLDING_REGISTER | 5894 | 1 |  | s32 | -10000 | 10000 | 100
id:28552 | MODBUS_HOLDING_REGISTER | 5896 | 1 |  | s32 | -10000 | 10000 | 100
id:28553 | MODBUS_HOLDING_REGISTER | 5898 | 1 |  | s32 | -10000 | 10000 | 100
id:28554 | MODBUS_HOLDING_REGISTER | 5900 | 1 |  | s32 | -10000 | 10000 | 100
id:28555 | MODBUS_HOLDING_REGISTER | 5902 | 1 |  | s32 | -10000 | 10000 | 100
id:28556 | MODBUS_HOLDING_REGISTER | 5904 | 1 |  | s32 | -10000 | 10000 | 100
id:28557 | MODBUS_HOLDING_REGISTER | 5906 | 1 |  | s32 | -10000 | 10000 | 100
id:28558 | MODBUS_HOLDING_REGISTER | 5908 | 1 |  | s32 | -10000 | 10000 | 100
id:28559 | MODBUS_HOLDING_REGISTER | 5910 | 1 |  | s32 | -10000 | 10000 | 100
id:28560 | MODBUS_HOLDING_REGISTER | 5912 | 1 |  | s32 | -10000 | 10000 | 100
id:28561 | MODBUS_HOLDING_REGISTER | 5914 | 1 |  | s32 | -10000 | 10000 | 100
id:28562 | MODBUS_HOLDING_REGISTER | 5916 | 1 |  | s32 | -10000 | 10000 | 100
id:28563 | MODBUS_HOLDING_REGISTER | 5918 | 1 |  | s32 | -10000 | 10000 | 100
id:28564 | MODBUS_HOLDING_REGISTER | 5920 | 1 |  | s32 | -10000 | 10000 | 100
id:28565 | MODBUS_HOLDING_REGISTER | 5922 | 1 |  | s32 | -10000 | 10000 | 100
id:28566 | MODBUS_HOLDING_REGISTER | 5924 | 1 |  | s32 | -10000 | 10000 | 100
id:28567 | MODBUS_HOLDING_REGISTER | 5926 | 1 |  | s32 | -10000 | 10000 | 100
id:28568 | MODBUS_HOLDING_REGISTER | 5928 | 1 |  | s32 | -10000 | 10000 | 100
id:28569 | MODBUS_HOLDING_REGISTER | 5930 | 1 |  | s32 | -10000 | 10000 | 100
id:28570 | MODBUS_HOLDING_REGISTER | 5932 | 1 |  | s32 | -10000 | 10000 | 100
id:28571 | MODBUS_HOLDING_REGISTER | 5934 | 1 |  | s32 | -10000 | 10000 | 100
id:28572 | MODBUS_HOLDING_REGISTER | 5936 | 1 |  | s32 | -10000 | 10000 | 100
id:28573 | MODBUS_HOLDING_REGISTER | 5938 | 1 |  | s32 | -10000 | 10000 | 100
id:28574 | MODBUS_HOLDING_REGISTER | 5940 | 1 |  | s32 | -10000 | 10000 | 100
id:28575 | MODBUS_HOLDING_REGISTER | 5942 | 1 |  | s32 | -10000 | 10000 | 100
id:28576 | MODBUS_HOLDING_REGISTER | 5944 | 1 |  | s32 | -10000 | 10000 | 100
id:28577 | MODBUS_HOLDING_REGISTER | 5946 | 1 |  | s32 | -10000 | 10000 | 100
id:28578 | MODBUS_HOLDING_REGISTER | 5948 | 1 |  | s32 | -10000 | 10000 | 100
id:28579 | MODBUS_HOLDING_REGISTER | 5950 | 1 |  | s32 | -10000 | 10000 | 100
id:28580 | MODBUS_HOLDING_REGISTER | 5952 | 1 |  | s32 | -10000 | 10000 | 100
id:28581 | MODBUS_HOLDING_REGISTER | 5954 | 1 |  | s32 | -10000 | 10000 | 100
id:28582 | MODBUS_HOLDING_REGISTER | 5956 | 1 |  | s32 | -10000 | 10000 | 100
id:28583 | MODBUS_HOLDING_REGISTER | 5958 | 1 |  | s32 | -10000 | 10000 | 100
id:28584 | MODBUS_HOLDING_REGISTER | 5960 | 1 |  | s32 | -10000 | 10000 | 100
id:28585 | MODBUS_HOLDING_REGISTER | 5962 | 1 |  | s32 | -10000 | 10000 | 100
id:28586 | MODBUS_HOLDING_REGISTER | 5964 | 1 |  | s32 | -10000 | 10000 | 100
id:28587 | MODBUS_HOLDING_REGISTER | 5966 | 1 |  | s32 | -10000 | 10000 | 100
id:28588 | MODBUS_HOLDING_REGISTER | 5968 | 1 |  | s32 | -10000 | 10000 | 100
id:28589 | MODBUS_HOLDING_REGISTER | 5970 | 1 |  | s32 | -10000 | 10000 | 100
id:28590 | MODBUS_HOLDING_REGISTER | 5972 | 1 |  | s32 | -10000 | 10000 | 100
id:28591 | MODBUS_HOLDING_REGISTER | 5974 | 1 |  | s32 | -10000 | 10000 | 100
id:28592 | MODBUS_HOLDING_REGISTER | 5976 | 1 |  | s32 | -10000 | 10000 | 100
id:28593 | MODBUS_HOLDING_REGISTER | 5978 | 1 |  | s32 | -10000 | 10000 | 100
id:28594 | MODBUS_HOLDING_REGISTER | 5980 | 1 |  | s32 | -10000 | 10000 | 100
id:28595 | MODBUS_HOLDING_REGISTER | 5982 | 1 |  | s32 | -10000 | 10000 | 100
id:29258 | MODBUS_HOLDING_REGISTER | 5984 | 1 | kW | u16 | 0 | 65535 | 0
Current power | MODBUS_INPUT_REGISTER | 2727 | 100 | kW | u32 | 0 | 0 | 0
id:29292 | MODBUS_HOLDING_REGISTER | 5985 | 1 |  | s16 | 0 | 20 | 0
id:29970 | MODBUS_HOLDING_REGISTER | 5986 | 1 |  | u8 | 0 | 1 | 0
id:29971 | MODBUS_HOLDING_REGISTER | 5987 | 10 | °C | s16 | 0 | 0 | 0
Input AUX7 | MODBUS_HOLDING_REGISTER | 1555 | 1 |  | u8 | 0 | 68 | 0
Input AUX8 | MODBUS_HOLDING_REGISTER | 1556 | 1 |  | u8 | 0 | 68 | 0
Input AUX9 | MODBUS_HOLDING_REGISTER | 1557 | 1 |  | u8 | 0 | 68 | 0
id:55076 | MODBUS_HOLDING_REGISTER | 2877 | 1 |  | u8 | 0 | 1 | 0
id:55077 | MODBUS_HOLDING_REGISTER | 2878 | 1 |  | u8 | 0 | 1 | 0
id:55078 | MODBUS_HOLDING_REGISTER | 2879 | 1 |  | u8 | 0 | 1 | 0
id:55079 | MODBUS_HOLDING_REGISTER | 2880 | 1 |  | u8 | 0 | 1 | 0
id:55080 | MODBUS_HOLDING_REGISTER | 2881 | 1 |  | u8 | 0 | 1 | 0
id:55081 | MODBUS_HOLDING_REGISTER | 2882 | 1 |  | u8 | 0 | 1 | 0
id:55082 | MODBUS_HOLDING_REGISTER | 2883 | 1 |  | u8 | 0 | 1 | 0
id:55083 | MODBUS_HOLDING_REGISTER | 2884 | 1 |  | u8 | 0 | 1 | 0
Immersion heater power, emergency mode | MODBUS_HOLDING_REGISTER | 3028 | 100 | kW | s16 | 0 | 4500 | 940
Disable emergency restart GP1 | MODBUS_HOLDING_REGISTER | 3986 | 1 |  | u8 | 0 | 1 | 0
EEV Control Mode (EB101) | MODBUS_INPUT_REGISTER | 2413 | 1 |  | u8 | 0 | 0 | 0
EEV State (EB101) | MODBUS_INPUT_REGISTER | 2421 | 1 |  | u8 | 0 | 0 | 0
id:55495 | MODBUS_HOLDING_REGISTER | 5550 | 1 |  | u8 | 0 | 1 | 0
id:55496 | MODBUS_HOLDING_REGISTER | 5207 | 10 | °C | s16 | 0 | 0 | 0
id:55749 | MODBUS_HOLDING_REGISTER | 5551 | 1 |  | u8 | 0 | 1 | 0

## modbus_addresses_common (2)
Title | Register type | Register | Division factor | Unit | Size of variable | Min value | Max value | Default value | Column1
Current outdoor temperature (BT1) | MODBUS_INPUT_REGISTER | 1 | 10 | °C | s16 | 0 | 0 | 0
Average temperature (BT1) | MODBUS_INPUT_REGISTER | 37 | 10 | °C | s16 | 0 | 0 | 0
External supply line (BT25) | MODBUS_INPUT_REGISTER | 39 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 60 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 61 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 62 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 63 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 64 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 65 | 10 | °C | s16 | 0 | 0 | 0
Return line (BT71) | MODBUS_INPUT_REGISTER | 88 | 10 | °C | s16 | 0 | 0 | 0
Degree minutes | MODBUS_HOLDING_REGISTER | 11 | 10 | DM | s32 | -30000 | 30000 | 0
Injection (EB101-BT81) | MODBUS_INPUT_REGISTER | 552 | 10 | °C | s16 | 0 | 0 | 0
Evaporator (EB101-BT84) | MODBUS_INPUT_REGISTER | 555 | 10 | °C | s16 | 0 | 0 | 0
Calculated supply climate system 1 | MODBUS_INPUT_REGISTER | 1017 | 10 | °C | s16 | 0 | 0 | 0
Operating mode internal add. heat | MODBUS_INPUT_REGISTER | 1029 | 1 |  | u8 | 0 | 0 | 0
External heating medium pump (GP10) status | MODBUS_INPUT_REGISTER | 1066 | 1 |  | u8 | 0 | 0 | 0
Return line (EB101-BT3) | MODBUS_INPUT_REGISTER | 1475 | 10 | °C | s16 | 0 | 0 | 0
Condenser sensor, supply line (EB101-BT12) | MODBUS_INPUT_REGISTER | 1478 | 10 | °C | s16 | 0 | 0 | 0
Discharge (EB101-BT14) | MODBUS_INPUT_REGISTER | 1479 | 10 | °C | s16 | 0 | 0 | 0
Liquid line (EB101-BT15) | MODBUS_INPUT_REGISTER | 1480 | 10 | °C | s16 | 0 | 0 | 0
Suction gas (EB101-BT17) | MODBUS_INPUT_REGISTER | 1481 | 10 | °C | s16 | 0 | 0 | 0
Outdoor temperature (EB101-BT28) | MODBUS_INPUT_REGISTER | 1621 | 10 | °C | s16 | 0 | 0 | 0
Evaporator (EB101-BT16) | MODBUS_INPUT_REGISTER | 1622 | 10 | °C | s16 | 0 | 0 | 0
Charge pump speed (EB101-GP12) | MODBUS_INPUT_REGISTER | 1636 | 1 | % | u8 | 0 | 0 | 0
Low pressure (EB101-BP8) | MODBUS_INPUT_REGISTER | 1802 | 10 | bar | s16 | 0 | 0 | 0
Current compressor frequency (EB101) | MODBUS_INPUT_REGISTER | 1803 | 10 | Hz | s16 | 0 | 0 | 0
Protection mode (EB101) | MODBUS_INPUT_REGISTER | 1804 | 1 |  | u16 | 0 | 0 | 0
Requested compressor frequency (EB101) | MODBUS_INPUT_REGISTER | 1854 | 1 | Hz | u8 | 0 | 0 | 0
Evaporator 2 (EB101-EP14-BT16) | MODBUS_INPUT_REGISTER | 1966 | 10 | °C | s16 | 0 | 0 | 0
Alarm number | MODBUS_INPUT_REGISTER | 1975 | 1 |  | s16 | 0 | 0 | 0
id:27814 | MODBUS_INPUT_REGISTER | 46 | 10 | A | u32 | 0 | 0 | 0
id:27815 | MODBUS_INPUT_REGISTER | 48 | 10 | A | u32 | 0 | 0 | 0
id:27816 | MODBUS_INPUT_REGISTER | 50 | 10 | A | u32 | 0 | 0 | 0

## modbus_addresses_all
Title | Register type | Register | Division factor | Unit | Size of variable | Min value | Max value | Default value | Column1
Current outdoor temperature (BT1) | MODBUS_INPUT_REGISTER | 1 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP23-BT2) | MODBUS_INPUT_REGISTER | 2 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP22-BT2) | MODBUS_INPUT_REGISTER | 3 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP21-BT2) | MODBUS_INPUT_REGISTER | 4 | 10 | °C | s16 | 0 | 0 | 0
Collector in (AZ10-BT26) | MODBUS_INPUT_REGISTER | 21 | 10 | °C | s16 | 0 | 0 | 0
Collector out (AZ10-BT27) | MODBUS_INPUT_REGISTER | 22 | 10 | °C | s16 | 0 | 0 | 0
Return line (EQ1-BT65) | MODBUS_INPUT_REGISTER | 31 | 10 | °C | s16 | 0 | 0 | 0
Temperature limiter (EB100-FD1) | MODBUS_INPUT_REGISTER | 36 | 1 |  | s16 | 0 | 0 | 0
Average temperature (BT1) | MODBUS_INPUT_REGISTER | 37 | 10 | °C | s16 | 0 | 0 | 0
Boiler temperature (BT52) | MODBUS_INPUT_REGISTER | 38 | 10 | °C | s16 | 0 | 0 | 0
External supply line (BT25) | MODBUS_INPUT_REGISTER | 39 | 10 | °C | s16 | 0 | 0 | 0
Electrical anode (EB100-FR1) | MODBUS_INPUT_REGISTER | 41 | 1 |  | s16 | 0 | 0 | 0
Pool (CL12-BT51) | MODBUS_INPUT_REGISTER | 59 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 60 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 61 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 62 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 63 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 64 | 10 | °C | s16 | 0 | 0 | 0
- | MODBUS_INPUT_REGISTER | 65 | 10 | °C | s16 | 0 | 0 | 0
Collector in (AZ13-BT26) | MODBUS_INPUT_REGISTER | 66 | 10 | °C | s16 | 0 | 0 | 0
Collector in (AZ12-BT26) | MODBUS_INPUT_REGISTER | 67 | 10 | °C | s16 | 0 | 0 | 0
Collector in (AZ11-BT26) | MODBUS_INPUT_REGISTER | 68 | 10 | °C | s16 | 0 | 0 | 0
Collector out (AZ13-BT27) | MODBUS_INPUT_REGISTER | 69 | 10 | °C | s16 | 0 | 0 | 0
Collector out (AZ12-BT27) | MODBUS_INPUT_REGISTER | 70 | 10 | °C | s16 | 0 | 0 | 0
Collector out (AZ11-BT27) | MODBUS_INPUT_REGISTER | 71 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP23-BT3) | MODBUS_INPUT_REGISTER | 75 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP22-BT3) | MODBUS_INPUT_REGISTER | 76 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP21-BT3) | MODBUS_INPUT_REGISTER | 77 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP15-BT3) | MODBUS_INPUT_REGISTER | 78 | 10 | °C | s16 | 0 | 0 | 0
Outgoing hot water (BT70) | MODBUS_INPUT_REGISTER | 87 | 10 | °C | s16 | 0 | 0 | 0
Return line (BT71) | MODBUS_INPUT_REGISTER | 88 | 10 | °C | s16 | 0 | 0 | 0
Collector (EQ1-BT57) | MODBUS_INPUT_REGISTER | 90 | 10 | °C | s16 | 0 | 0 | 0
Heating dump (EQ1-BT75) | MODBUS_INPUT_REGISTER | 91 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP47-BT2) | MODBUS_INPUT_REGISTER | 94 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP46-BT2) | MODBUS_INPUT_REGISTER | 95 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP45-BT2) | MODBUS_INPUT_REGISTER | 96 | 10 | °C | s16 | 0 | 0 | 0
Supply line (EP44-BT2) | MODBUS_INPUT_REGISTER | 97 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP47-BT3) | MODBUS_INPUT_REGISTER | 98 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP46-BT3) | MODBUS_INPUT_REGISTER | 99 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP45-BT3) | MODBUS_INPUT_REGISTER | 100 | 10 | °C | s16 | 0 | 0 | 0
Return line (EP44-BT3) | MODBUS_INPUT_REGISTER | 101 | 10 | °C | s16 | 0 | 0 | 0
id:149 | MODBUS_INPUT_REGISTER | 108 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 8 (BT50) | MODBUS_INPUT_REGISTER | 109 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 7 (BT50) | MODBUS_INPUT_REGISTER | 110 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 6 (BT50) | MODBUS_INPUT_REGISTER | 111 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 5 (BT50) | MODBUS_INPUT_REGISTER | 112 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 4 (BT50) | MODBUS_INPUT_REGISTER | 113 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 3 (BT50) | MODBUS_INPUT_REGISTER | 114 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 2 (BT50) | MODBUS_INPUT_REGISTER | 115 | 10 | °C | s16 | 0 | 0 | 0
Room average temp. clim. system 1 (BT50) | MODBUS_INPUT_REGISTER | 116 | 10 | °C | s16 | 0 | 0 | 0
id:193 | MODBUS_INPUT_REGISTER | 128 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 8 | MODBUS_INPUT_REGISTER | 129 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 7 | MODBUS_INPUT_REGISTER | 130 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 6 | MODBUS_INPUT_REGISTER | 131 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 5 | MODBUS_INPUT_REGISTER | 132 | 1 |  | u8 | 0 | 0 | 0
id:246 | MODBUS_INPUT_REGISTER | 133 | 1 |  | u8 | 0 | 0 | 0
Relay status (ERS 1) | MODBUS_INPUT_REGISTER | 134 | 1 |  | u8 | 0 | 0 | 0
Fan speed (AZ30-GQ2) | MODBUS_INPUT_REGISTER | 135 | 1 | % | u8 | 0 | 0 | 0
Fan speed (AZ30-GQ3) | MODBUS_INPUT_REGISTER | 136 | 1 | % | u8 | 0 | 0 | 0
Current hot water mode controlled by | MODBUS_INPUT_REGISTER | 137 | 1 |  | s8 | 0 | 0 | 0
Max. compressor frequency, heating | MODBUS_INPUT_REGISTER | 141 | 100 | Hz | u16 | 0 | 0 | 0
External adjustment climate system 8 | MODBUS_INPUT_REGISTER | 151 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 7 | MODBUS_INPUT_REGISTER | 152 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 6 | MODBUS_INPUT_REGISTER | 153 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 5 | MODBUS_INPUT_REGISTER | 154 | 1 |  | u8 | 0 | 0 | 0
Climate system 8 | MODBUS_INPUT_REGISTER | 156 | 1 |  | u8 | 0 | 0 | 0
Climate system 7 | MODBUS_INPUT_REGISTER | 157 | 1 |  | u8 | 0 | 0 | 0
Climate system 6 | MODBUS_INPUT_REGISTER | 158 | 1 |  | u8 | 0 | 0 | 0
Climate system 5 | MODBUS_INPUT_REGISTER | 159 | 1 |  | u8 | 0 | 0 | 0
Extra cooling | MODBUS_INPUT_REGISTER | 160 | 1 |  | u8 | 0 | 0 | 0
Hot water comfort return (BT82) | MODBUS_INPUT_REGISTER | 174 | 10 | °C | s16 | 0 | 0 | 0
Hot water comfort heater (BT83) | MODBUS_INPUT_REGISTER | 175 | 10 | °C | s16 | 0 | 0 | 0
Compressor, total time pool, heat pump 8 (EP15) | MODBUS_INPUT_REGISTER | 179 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 8 (EP15) | MODBUS_INPUT_REGISTER | 181 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 8 (EP14) | MODBUS_INPUT_REGISTER | 185 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 8 (EP14) | MODBUS_INPUT_REGISTER | 187 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 7 (EP15) | MODBUS_INPUT_REGISTER | 191 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 7 (EP15) | MODBUS_INPUT_REGISTER | 193 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 7 (EP14) | MODBUS_INPUT_REGISTER | 197 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 7 (EP14) | MODBUS_INPUT_REGISTER | 199 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 6 (EP15) | MODBUS_INPUT_REGISTER | 203 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 6 (EP15) | MODBUS_INPUT_REGISTER | 205 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 6 (EP14) | MODBUS_INPUT_REGISTER | 209 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 6 (EP14) | MODBUS_INPUT_REGISTER | 211 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 5 (EP15) | MODBUS_INPUT_REGISTER | 215 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 5 (EP15) | MODBUS_INPUT_REGISTER | 217 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 5 (EP14) | MODBUS_INPUT_REGISTER | 221 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 5 (EP14) | MODBUS_INPUT_REGISTER | 223 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 4 (EP15) | MODBUS_INPUT_REGISTER | 227 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 4 (EP15) | MODBUS_INPUT_REGISTER | 229 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 4 (EP14) | MODBUS_INPUT_REGISTER | 233 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 4 (EP14) | MODBUS_INPUT_REGISTER | 235 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 3 (EP15) | MODBUS_INPUT_REGISTER | 239 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 3 (EP15) | MODBUS_INPUT_REGISTER | 241 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 3 (EP14) | MODBUS_INPUT_REGISTER | 245 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 3 (EP14) | MODBUS_INPUT_REGISTER | 247 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 2 (EP15) | MODBUS_INPUT_REGISTER | 251 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 2 (EP15) | MODBUS_INPUT_REGISTER | 253 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 2 (EP14) | MODBUS_INPUT_REGISTER | 257 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 2 (EP14) | MODBUS_INPUT_REGISTER | 259 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, heat pump 1 (EP15) | MODBUS_INPUT_REGISTER | 263 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool 2, heat pump 1 (EP15) | MODBUS_INPUT_REGISTER | 265 | 1 | h | u32 | 0 | 0 | 0
Compressor, total time pool, heat pump 1 (EP14) | MODBUS_INPUT_REGISTER | 269 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, heat pump 1 (EP14) | MODBUS_INPUT_REGISTER | 271 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time cooling, main unit (EP14) | MODBUS_INPUT_REGISTER | 279 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool, main unit (EP14) | MODBUS_INPUT_REGISTER | 281 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time pool 2, main unit (EP14) | MODBUS_INPUT_REGISTER | 283 | 1 | h | u32 | 0 | 2147483647 | 0
Heat pump 8 requested compressor frequency | MODBUS_INPUT_REGISTER | 294 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 7 requested compressor frequency | MODBUS_INPUT_REGISTER | 295 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 6 requested compressor frequency | MODBUS_INPUT_REGISTER | 296 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 5 requested compressor frequency | MODBUS_INPUT_REGISTER | 297 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 4 requested compressor frequency | MODBUS_INPUT_REGISTER | 298 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 3 requested compressor frequency | MODBUS_INPUT_REGISTER | 299 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 2 requested compressor frequency | MODBUS_INPUT_REGISTER | 300 | 1 | Hz | u8 | 0 | 0 | 0
Heat pump 1 requested compressor frequency | MODBUS_INPUT_REGISTER | 301 | 1 | Hz | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 8 | MODBUS_INPUT_REGISTER | 303 | 1 |  | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 7 | MODBUS_INPUT_REGISTER | 304 | 1 |  | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 6 | MODBUS_INPUT_REGISTER | 305 | 1 |  | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 5 | MODBUS_INPUT_REGISTER | 306 | 1 |  | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 4 | MODBUS_INPUT_REGISTER | 307 | 1 |  | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 3 | MODBUS_INPUT_REGISTER | 308 | 1 |  | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 2 | MODBUS_INPUT_REGISTER | 309 | 1 |  | u8 | 0 | 0 | 0
Status (OPT) | MODBUS_INPUT_REGISTER | 311 | 1 |  | u8 | 0 | 0 | 0
Version (OPT) | MODBUS_INPUT_REGISTER | 312 | 1 |  | u16 | 0 | 0 | 0
OPT relay, modulation level | MODBUS_INPUT_REGISTER | 313 | 10 | % | s16 | 0 | 0 | 0
OPT operating time | MODBUS_INPUT_REGISTER | 315 | 1 | h | u16 | 0 | 0 | 0
Available compressors heating | MODBUS_INPUT_REGISTER | 317 | 1 |  | u8 | 0 | 0 | 0
Available compressors hot water | MODBUS_INPUT_REGISTER | 318 | 1 |  | u8 | 0 | 0 | 0
Available compressors pool 1 | MODBUS_INPUT_REGISTER | 319 | 1 |  | u8 | 0 | 0 | 0
Available compressors pool 2 | MODBUS_INPUT_REGISTER | 320 | 1 |  | u8 | 0 | 0 | 0
Available compressors cooling | MODBUS_INPUT_REGISTER | 321 | 1 |  | u8 | 0 | 0 | 0
Supply temperature (BT64) | MODBUS_INPUT_REGISTER | 337 | 10 | °C | s16 | 0 | 0 | 0
Heat pump functionality 2 | MODBUS_INPUT_REGISTER | 338 | 1 |  | u32 | 0 | 0 | 0
Status (S135) | MODBUS_INPUT_REGISTER | 344 | 1 |  | u8 | 0 | 0 | 0
Status, demand, pump speed (S135) | MODBUS_INPUT_REGISTER | 345 | 1 |  | u8 | 0 | 0 | 0
Status, demand, fan speed (S135) | MODBUS_INPUT_REGISTER | 346 | 1 |  | u8 | 0 | 0 | 0
Status, solenoid (S135) | MODBUS_INPUT_REGISTER | 347 | 1 |  | u8 | 0 | 0 | 0
Status, compressor, heater(S135) | MODBUS_INPUT_REGISTER | 348 | 1 |  | u8 | 0 | 0 | 0
Status, compressor, demand (S135) | MODBUS_INPUT_REGISTER | 350 | 1 |  | u8 | 0 | 0 | 0
Degree minutes | MODBUS_HOLDING_REGISTER | 11 | 10 | DM | s32 | -30000 | 30000 | 0
Blocking (ERS 1) | MODBUS_INPUT_REGISTER | 358 | 1 |  | u8 | 0 | 0 | 0
AZ30-EB17 | MODBUS_INPUT_REGISTER | 359 | 1 |  | u8 | 0 | 0 | 0
Supply line (S135-BT12) | MODBUS_INPUT_REGISTER | 360 | 10 | °C | s16 | 0 | 0 | 0
Return line (S135-BT13) | MODBUS_INPUT_REGISTER | 361 | 10 | °C | s16 | 0 | 0 | 0
Evaporator (S135-BT16) | MODBUS_INPUT_REGISTER | 362 | 10 | °C | s16 | 0 | 0 | 0
Defrosting sensor (S135-BT76) | MODBUS_INPUT_REGISTER | 363 | 10 | °C | s16 | 0 | 0 | 0
Incoming air (S135-BT77) | MODBUS_INPUT_REGISTER | 364 | 10 | °C | s16 | 0 | 0 | 0
Alarm number (S135) | MODBUS_INPUT_REGISTER | 365 | 1 |  | u16 | 0 | 0 | 0
Defrosting (S135) | MODBUS_INPUT_REGISTER | 366 | 1 |  | u8 | 0 | 0 | 0
Status, relay 5 (S135) | MODBUS_INPUT_REGISTER | 367 | 1 |  | u8 | 0 | 0 | 0
Status, relay 4 (S135) | MODBUS_INPUT_REGISTER | 368 | 1 |  | u8 | 0 | 0 | 0
Status, relay 3 (S135) | MODBUS_INPUT_REGISTER | 369 | 1 |  | u8 | 0 | 0 | 0
Status, relay 2 (S135) | MODBUS_INPUT_REGISTER | 370 | 1 |  | u8 | 0 | 0 | 0
Status, relay 1 (S135) | MODBUS_INPUT_REGISTER | 371 | 1 |  | u8 | 0 | 0 | 0
Status, relay 0 (S135) | MODBUS_INPUT_REGISTER | 372 | 1 |  | u8 | 0 | 0 | 0
Pump speed (S135) | MODBUS_INPUT_REGISTER | 373 | 1 | % | u8 | 0 | 0 | 0
Selected fan speed | MODBUS_INPUT_REGISTER | 374 | 1 | % | u8 | 0 | 0 | 0
Version (S135) | MODBUS_INPUT_REGISTER | 376 | 1 |  | u16 | 0 | 0 | 0
id:803 | MODBUS_INPUT_REGISTER | 377 | 1 |  | u32 | 0 | 2147483647 | 0
id:804 | MODBUS_INPUT_REGISTER | 379 | 1 |  | u32 | 0 | 0 | 0
id:805 | MODBUS_INPUT_REGISTER | 381 | 1 |  | u32 | 0 | 2147483647 | 0
id:806 | MODBUS_INPUT_REGISTER | 383 | 1 |  | u32 | 0 | 0 | 0
Seconds of blank time left, charge pump 8 | MODBUS_INPUT_REGISTER | 385 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 7 | MODBUS_INPUT_REGISTER | 386 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 6 | MODBUS_INPUT_REGISTER | 387 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 5 | MODBUS_INPUT_REGISTER | 388 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 4 | MODBUS_INPUT_REGISTER | 389 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 3 | MODBUS_INPUT_REGISTER | 390 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 2 | MODBUS_INPUT_REGISTER | 391 | 1 |  | u8 | 0 | 0 | 0
Seconds of blank time left, charge pump 1 | MODBUS_INPUT_REGISTER | 392 | 1 |  | u8 | 0 | 0 | 0
Alarm number from outdoor air heat pump (EB101) | MODBUS_INPUT_REGISTER | 400 | 1 |  | u8 | 0 | 0 | 0
Fan speed (EB101) | MODBUS_INPUT_REGISTER | 401 | 1 | rpm | u16 | 0 | 0 | 0
Max fan speed (EB101) | MODBUS_INPUT_REGISTER | 402 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB101) | MODBUS_INPUT_REGISTER | 403 | 1 | rpm | u16 | 0 | 0 | 0
Max compressor speed (EB101) | MODBUS_INPUT_REGISTER | 404 | 10 | Hz | u16 | 0 | 0 | 0
Min compressor speed (EB101) | MODBUS_INPUT_REGISTER | 405 | 10 | Hz | u16 | 0 | 0 | 0
Generated power heating (EB101) | MODBUS_INPUT_REGISTER | 406 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB101) | MODBUS_INPUT_REGISTER | 407 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB101) | MODBUS_INPUT_REGISTER | 408 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB101) | MODBUS_INPUT_REGISTER | 409 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB101) | MODBUS_INPUT_REGISTER | 410 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB101) | MODBUS_INPUT_REGISTER | 411 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB101) | MODBUS_INPUT_REGISTER | 412 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB101) | MODBUS_INPUT_REGISTER | 413 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB101) | MODBUS_INPUT_REGISTER | 414 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB101) | MODBUS_INPUT_REGISTER | 415 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB101) | MODBUS_INPUT_REGISTER | 416 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB101) | MODBUS_INPUT_REGISTER | 417 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB101) | MODBUS_INPUT_REGISTER | 418 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB101) | MODBUS_INPUT_REGISTER | 419 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB101) | MODBUS_INPUT_REGISTER | 420 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB101) | MODBUS_INPUT_REGISTER | 421 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB101) | MODBUS_INPUT_REGISTER | 422 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open in (EVI)(EB101) | MODBUS_INPUT_REGISTER | 423 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB101) | MODBUS_INPUT_REGISTER | 424 | 1 |  | u16 | 0 | 0 | 0
id:859 | MODBUS_INPUT_REGISTER | 426 | 10 | %RH | s16 | 0 | 0 | 0
id:861 | MODBUS_INPUT_REGISTER | 427 | 1 |  | u32 | 0 | 0 | 0
id:862 | MODBUS_INPUT_REGISTER | 429 | 1 |  | u16 | 0 | 0 | 0
Low press (EB108 BP8 dew) | MODBUS_INPUT_REGISTER | 438 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB108 BP9 dew) | MODBUS_INPUT_REGISTER | 439 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB108-BP11) | MODBUS_INPUT_REGISTER | 441 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB108-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 442 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB108-EP14) | MODBUS_INPUT_REGISTER | 444 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB108-EP14) | MODBUS_INPUT_REGISTER | 445 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB107 BP8 dew) | MODBUS_INPUT_REGISTER | 454 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB107 BP9 dew) | MODBUS_INPUT_REGISTER | 455 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB107-BP11) | MODBUS_INPUT_REGISTER | 457 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB107-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 458 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB107-EP14) | MODBUS_INPUT_REGISTER | 460 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB107-EP14) | MODBUS_INPUT_REGISTER | 461 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB106 BP8 dew) | MODBUS_INPUT_REGISTER | 470 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB106 BP9 dew) | MODBUS_INPUT_REGISTER | 471 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB106-BP11) | MODBUS_INPUT_REGISTER | 473 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB106-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 474 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB106-EP14) | MODBUS_INPUT_REGISTER | 476 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB106-EP14) | MODBUS_INPUT_REGISTER | 477 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB105 BP8 dew) | MODBUS_INPUT_REGISTER | 486 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB105 BP9 dew) | MODBUS_INPUT_REGISTER | 487 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB105-BP11) | MODBUS_INPUT_REGISTER | 489 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB105-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 490 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB105-EP14) | MODBUS_INPUT_REGISTER | 492 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB105-EP14) | MODBUS_INPUT_REGISTER | 493 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB104 BP8 dew) | MODBUS_INPUT_REGISTER | 502 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB104 BP9 dew) | MODBUS_INPUT_REGISTER | 503 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB104-BP11) | MODBUS_INPUT_REGISTER | 505 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB104-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 506 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB104-EP14) | MODBUS_INPUT_REGISTER | 508 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB104-EP14) | MODBUS_INPUT_REGISTER | 509 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB103 BP8 dew) | MODBUS_INPUT_REGISTER | 518 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB103 BP9 dew) | MODBUS_INPUT_REGISTER | 519 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB103-BP11) | MODBUS_INPUT_REGISTER | 521 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB103-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 522 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB103-EP14) | MODBUS_INPUT_REGISTER | 524 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB103-EP14) | MODBUS_INPUT_REGISTER | 525 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB102 BP8 dew) | MODBUS_INPUT_REGISTER | 534 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB102 BP9 dew) | MODBUS_INPUT_REGISTER | 535 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB102-EP14-BP11) | MODBUS_INPUT_REGISTER | 537 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB102-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 538 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB102-EP14) | MODBUS_INPUT_REGISTER | 540 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB102-EP14) | MODBUS_INPUT_REGISTER | 541 | 1 | rpm | u16 | 0 | 0 | 0
Low press (EB101 BP8 dew) | MODBUS_INPUT_REGISTER | 550 | 10 | °C | s16 | 0 | 0 | 0
Hi press (EB101 BP9 dew) | MODBUS_INPUT_REGISTER | 551 | 10 | °C | s16 | 0 | 0 | 0
Injection (EB101-BT81) | MODBUS_INPUT_REGISTER | 552 | 10 | °C | s16 | 0 | 0 | 0
Pressure sensor, injection (EB101-BP11) | MODBUS_INPUT_REGISTER | 553 | 10 |  | s16 | 0 | 0 | 0
EVI pressure (EB101-EP14-BP11 dew) | MODBUS_INPUT_REGISTER | 554 | 10 | °C | s16 | 0 | 0 | 0
Evaporator (EB101-BT84) | MODBUS_INPUT_REGISTER | 555 | 10 | °C | s16 | 0 | 0 | 0
Fan status (EB101-EP14) | MODBUS_INPUT_REGISTER | 556 | 1 |  | u8 | 0 | 0 | 0
Fan rpm (EB101-EP14) | MODBUS_INPUT_REGISTER | 557 | 1 | rpm | u16 | 0 | 0 | 0
High condenser out alarm (S135) | MODBUS_INPUT_REGISTER | 575 | 1 |  | u16 | 0 | 0 | 0
High condenser in alarm (S135) | MODBUS_INPUT_REGISTER | 576 | 1 |  | u16 | 0 | 0 | 0
Operating mode PV panels | MODBUS_INPUT_REGISTER | 579 | 1 |  | u8 | 0 | 0 | 0
EME lux mode without EME | MODBUS_INPUT_REGISTER | 581 | 1 |  | u8 | 0 | 0 | 0
Timer (EME) | MODBUS_INPUT_REGISTER | 582 | 60 | min | u16 | 0 | 0 | 0
Fan mode 4 | MODBUS_INPUT_REGISTER | 590 | 1 | % | u8 | 0 | 0 | 0
Fan mode 3 | MODBUS_INPUT_REGISTER | 591 | 1 | % | u8 | 0 | 0 | 0
Fan mode 2 | MODBUS_INPUT_REGISTER | 592 | 1 | % | u8 | 0 | 0 | 0
Is the compressor accessible | MODBUS_INPUT_REGISTER | 593 | 1 |  | u8 | 0 | 0 | 0
Prio, hot water (OPT) | MODBUS_INPUT_REGISTER | 604 | 1 |  | u8 | 0 | 0 | 0
Permit (undefined) | MODBUS_INPUT_REGISTER | 683 | 1 |  | u8 | 0 | 0 | 0
Permit (undefined) | MODBUS_INPUT_REGISTER | 684 | 1 |  | u8 | 0 | 0 | 0
Permit (undefined) | MODBUS_INPUT_REGISTER | 685 | 1 |  | u8 | 0 | 0 | 0
Permit (OPT 10) additional heat | MODBUS_INPUT_REGISTER | 686 | 1 |  | u8 | 0 | 0 | 0
Permit ext. imm. heater step | MODBUS_INPUT_REGISTER | 687 | 1 |  | u8 | 0 | 0 | 0
Permit int. imm. heater step | MODBUS_INPUT_REGISTER | 688 | 1 |  | u8 | 0 | 0 | 0
Permit shunted additional heat | MODBUS_INPUT_REGISTER | 689 | 1 |  | u8 | 0 | 0 | 0
Permit prioritised additional heat | MODBUS_INPUT_REGISTER | 690 | 1 |  | u8 | 0 | 0 | 0
Permit (EB108-EP15) | MODBUS_INPUT_REGISTER | 691 | 1 |  | u8 | 0 | 0 | 0
Permit (EB107-EP15) | MODBUS_INPUT_REGISTER | 692 | 1 |  | u8 | 0 | 0 | 0
Permit (EB106-EP15) | MODBUS_INPUT_REGISTER | 693 | 1 |  | u8 | 0 | 0 | 0
Permit (EB105-EP15) | MODBUS_INPUT_REGISTER | 694 | 1 |  | u8 | 0 | 0 | 0
Permit (EB104-EP15) | MODBUS_INPUT_REGISTER | 695 | 1 |  | u8 | 0 | 0 | 0
Permit (EB103-EP15) | MODBUS_INPUT_REGISTER | 696 | 1 |  | u8 | 0 | 0 | 0
Permit (EB102-EP15) | MODBUS_INPUT_REGISTER | 697 | 1 |  | u8 | 0 | 0 | 0
Permit (EB101-EP15) | MODBUS_INPUT_REGISTER | 698 | 1 |  | u8 | 0 | 0 | 0
Permit (EB100-EP15) | MODBUS_INPUT_REGISTER | 699 | 1 |  | u8 | 0 | 0 | 0
Permit (EB108-EP14) | MODBUS_INPUT_REGISTER | 700 | 1 |  | u8 | 0 | 0 | 0
Permit (EB107-EP14) | MODBUS_INPUT_REGISTER | 701 | 1 |  | u8 | 0 | 0 | 0
Permit (EB106-EP14) | MODBUS_INPUT_REGISTER | 702 | 1 |  | u8 | 0 | 0 | 0
Permit (EB105-EP14) | MODBUS_INPUT_REGISTER | 703 | 1 |  | u8 | 0 | 0 | 0
Permit (EB104-EP14) | MODBUS_INPUT_REGISTER | 704 | 1 |  | u8 | 0 | 0 | 0
Permit (EB103-EP14) | MODBUS_INPUT_REGISTER | 705 | 1 |  | u8 | 0 | 0 | 0
Permit (EB102-EP14) | MODBUS_INPUT_REGISTER | 706 | 1 |  | u8 | 0 | 0 | 0
Permit (EB101-EP14) | MODBUS_INPUT_REGISTER | 707 | 1 |  | u8 | 0 | 0 | 0
Permit (EB100-EP14) | MODBUS_INPUT_REGISTER | 708 | 1 |  | u8 | 0 | 0 | 0
Smart energy source, priority 7, start DM | MODBUS_INPUT_REGISTER | 709 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 6, start DM | MODBUS_INPUT_REGISTER | 711 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 5, start DM | MODBUS_INPUT_REGISTER | 713 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 4, start DM | MODBUS_INPUT_REGISTER | 715 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 3, start DM | MODBUS_INPUT_REGISTER | 717 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 2, start DM | MODBUS_INPUT_REGISTER | 719 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 1, start DM | MODBUS_INPUT_REGISTER | 721 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 7, stop DM | MODBUS_INPUT_REGISTER | 723 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 6, stop DM | MODBUS_INPUT_REGISTER | 725 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 5, stop DM | MODBUS_INPUT_REGISTER | 727 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 4, stop DM | MODBUS_INPUT_REGISTER | 729 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 3, stop DM | MODBUS_INPUT_REGISTER | 731 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 2, stop DM | MODBUS_INPUT_REGISTER | 733 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, priority 1, stop DM | MODBUS_INPUT_REGISTER | 735 | 1 |  | s32 | 0 | 0 | 0
Smart energy source, DM minimum value | MODBUS_INPUT_REGISTER | 737 | 1 |  | s32 | 0 | 0 | 0
External guide status | MODBUS_INPUT_REGISTER | 745 | 1 |  | u8 | 0 | 0 | 0
Test guide value | MODBUS_INPUT_REGISTER | 746 | 1 |  | u16 | 0 | 0 | 0
Temp. lux forces start of hot water demand | MODBUS_INPUT_REGISTER | 747 | 1 |  | u8 | 0 | 0 | 0
Smart energy source, prio OPT10 for hot water | MODBUS_INPUT_REGISTER | 757 | 1 |  | u8 | 0 | 0 | 0
Wood boiler activated | MODBUS_INPUT_REGISTER | 759 | 1 |  | u8 | 0 | 0 | 0
Max fan speed (EB108-F21x0) | MODBUS_INPUT_REGISTER | 762 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB108) | MODBUS_INPUT_REGISTER | 763 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB108) | MODBUS_INPUT_REGISTER | 766 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB108) | MODBUS_INPUT_REGISTER | 767 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB108) | MODBUS_INPUT_REGISTER | 768 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB108) | MODBUS_INPUT_REGISTER | 769 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB108) | MODBUS_INPUT_REGISTER | 770 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB108) | MODBUS_INPUT_REGISTER | 771 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB108) | MODBUS_INPUT_REGISTER | 772 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB108) | MODBUS_INPUT_REGISTER | 773 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB108) | MODBUS_INPUT_REGISTER | 774 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB108) | MODBUS_INPUT_REGISTER | 775 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB108) | MODBUS_INPUT_REGISTER | 776 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB108) | MODBUS_INPUT_REGISTER | 777 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB108) | MODBUS_INPUT_REGISTER | 778 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB108) | MODBUS_INPUT_REGISTER | 779 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB108) | MODBUS_INPUT_REGISTER | 780 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB108) | MODBUS_INPUT_REGISTER | 781 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB108) | MODBUS_INPUT_REGISTER | 782 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB108) | MODBUS_INPUT_REGISTER | 783 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB108) | MODBUS_INPUT_REGISTER | 784 | 1 |  | u16 | 0 | 0 | 0
Max fan speed (EB107) | MODBUS_INPUT_REGISTER | 787 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB107) | MODBUS_INPUT_REGISTER | 788 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB107) | MODBUS_INPUT_REGISTER | 791 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB107) | MODBUS_INPUT_REGISTER | 792 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB107) | MODBUS_INPUT_REGISTER | 793 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB107) | MODBUS_INPUT_REGISTER | 794 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB107) | MODBUS_INPUT_REGISTER | 795 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB107) | MODBUS_INPUT_REGISTER | 796 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB107) | MODBUS_INPUT_REGISTER | 797 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB107) | MODBUS_INPUT_REGISTER | 798 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB107) | MODBUS_INPUT_REGISTER | 799 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB107) | MODBUS_INPUT_REGISTER | 800 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB107) | MODBUS_INPUT_REGISTER | 801 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB107) | MODBUS_INPUT_REGISTER | 802 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB107) | MODBUS_INPUT_REGISTER | 803 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB107) | MODBUS_INPUT_REGISTER | 804 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB107) | MODBUS_INPUT_REGISTER | 805 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB107) | MODBUS_INPUT_REGISTER | 806 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB107) | MODBUS_INPUT_REGISTER | 807 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB107) | MODBUS_INPUT_REGISTER | 808 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB107) | MODBUS_INPUT_REGISTER | 809 | 1 |  | u16 | 0 | 0 | 0
Max fan speed (EB106) | MODBUS_INPUT_REGISTER | 812 | 1 | rpm | u16 | 0 | 0 | 0
id:1309 | MODBUS_INPUT_REGISTER | 813 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB106) | MODBUS_INPUT_REGISTER | 816 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB106) | MODBUS_INPUT_REGISTER | 817 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB106) | MODBUS_INPUT_REGISTER | 818 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB106) | MODBUS_INPUT_REGISTER | 819 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB106) | MODBUS_INPUT_REGISTER | 820 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB106) | MODBUS_INPUT_REGISTER | 821 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB106) | MODBUS_INPUT_REGISTER | 822 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB106) | MODBUS_INPUT_REGISTER | 823 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB106) | MODBUS_INPUT_REGISTER | 824 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB106) | MODBUS_INPUT_REGISTER | 825 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB106) | MODBUS_INPUT_REGISTER | 826 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB106) | MODBUS_INPUT_REGISTER | 827 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB106) | MODBUS_INPUT_REGISTER | 828 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB106) | MODBUS_INPUT_REGISTER | 829 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB106) | MODBUS_INPUT_REGISTER | 830 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB106) | MODBUS_INPUT_REGISTER | 831 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB106) | MODBUS_INPUT_REGISTER | 832 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB106) | MODBUS_INPUT_REGISTER | 833 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB106) | MODBUS_INPUT_REGISTER | 834 | 1 |  | u16 | 0 | 0 | 0
Max fan speed (EB105) | MODBUS_INPUT_REGISTER | 837 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB105) | MODBUS_INPUT_REGISTER | 838 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB105) | MODBUS_INPUT_REGISTER | 841 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB105) | MODBUS_INPUT_REGISTER | 842 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB105) | MODBUS_INPUT_REGISTER | 843 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB105) | MODBUS_INPUT_REGISTER | 844 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB105) | MODBUS_INPUT_REGISTER | 845 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB105) | MODBUS_INPUT_REGISTER | 846 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB105) | MODBUS_INPUT_REGISTER | 847 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB105) | MODBUS_INPUT_REGISTER | 848 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB105) | MODBUS_INPUT_REGISTER | 849 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB105) | MODBUS_INPUT_REGISTER | 850 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB105) | MODBUS_INPUT_REGISTER | 851 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB105) | MODBUS_INPUT_REGISTER | 852 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB105) | MODBUS_INPUT_REGISTER | 853 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB105) | MODBUS_INPUT_REGISTER | 854 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB105) | MODBUS_INPUT_REGISTER | 855 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB105) | MODBUS_INPUT_REGISTER | 856 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB105) | MODBUS_INPUT_REGISTER | 857 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB105) | MODBUS_INPUT_REGISTER | 858 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB105) | MODBUS_INPUT_REGISTER | 859 | 1 |  | u16 | 0 | 0 | 0
Max fan speed (EB104) | MODBUS_INPUT_REGISTER | 862 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB104) | MODBUS_INPUT_REGISTER | 863 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB104) | MODBUS_INPUT_REGISTER | 866 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB104) | MODBUS_INPUT_REGISTER | 867 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB104) | MODBUS_INPUT_REGISTER | 868 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB104) | MODBUS_INPUT_REGISTER | 869 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB104) | MODBUS_INPUT_REGISTER | 870 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB104) | MODBUS_INPUT_REGISTER | 871 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB104) | MODBUS_INPUT_REGISTER | 872 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB104) | MODBUS_INPUT_REGISTER | 873 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB104) | MODBUS_INPUT_REGISTER | 874 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB104) | MODBUS_INPUT_REGISTER | 875 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB104) | MODBUS_INPUT_REGISTER | 876 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB104) | MODBUS_INPUT_REGISTER | 877 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB104) | MODBUS_INPUT_REGISTER | 878 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB104) | MODBUS_INPUT_REGISTER | 879 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB104) | MODBUS_INPUT_REGISTER | 880 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB104) | MODBUS_INPUT_REGISTER | 881 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB104) | MODBUS_INPUT_REGISTER | 882 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB104) | MODBUS_INPUT_REGISTER | 883 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB104) | MODBUS_INPUT_REGISTER | 884 | 1 |  | u16 | 0 | 0 | 0
Max fan speed (EB103) | MODBUS_INPUT_REGISTER | 887 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB103) | MODBUS_INPUT_REGISTER | 888 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB103) | MODBUS_INPUT_REGISTER | 891 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB103) | MODBUS_INPUT_REGISTER | 892 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB103) | MODBUS_INPUT_REGISTER | 893 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB103) | MODBUS_INPUT_REGISTER | 894 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB103) | MODBUS_INPUT_REGISTER | 895 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB103) | MODBUS_INPUT_REGISTER | 896 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB103) | MODBUS_INPUT_REGISTER | 897 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB103) | MODBUS_INPUT_REGISTER | 898 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB103) | MODBUS_INPUT_REGISTER | 899 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB103) | MODBUS_INPUT_REGISTER | 900 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB103) | MODBUS_INPUT_REGISTER | 901 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB103) | MODBUS_INPUT_REGISTER | 902 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB103) | MODBUS_INPUT_REGISTER | 903 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB103) | MODBUS_INPUT_REGISTER | 904 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB103) | MODBUS_INPUT_REGISTER | 905 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB103) | MODBUS_INPUT_REGISTER | 906 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB103) | MODBUS_INPUT_REGISTER | 907 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB103) | MODBUS_INPUT_REGISTER | 908 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB103) | MODBUS_INPUT_REGISTER | 909 | 1 |  | u16 | 0 | 0 | 0
Fan speed (EB102) | MODBUS_INPUT_REGISTER | 911 | 1 | rpm | u16 | 0 | 0 | 0
Max fan speed (EB102) | MODBUS_INPUT_REGISTER | 912 | 1 | rpm | u16 | 0 | 0 | 0
Min fan speed (EB102) | MODBUS_INPUT_REGISTER | 913 | 1 | rpm | u16 | 0 | 0 | 0
Generated power heating (EB102 | MODBUS_INPUT_REGISTER | 916 | 10 | kW | u16 | 0 | 0 | 0
Time to defrosting (EB102) | MODBUS_INPUT_REGISTER | 917 | 1 | min | u16 | 0 | 0 | 0
Defrosting index (EB102) | MODBUS_INPUT_REGISTER | 918 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EEV (EB102) | MODBUS_INPUT_REGISTER | 919 | 10 | °C | s16 | 0 | 0 | 0
Superheat EEV (EB102) | MODBUS_INPUT_REGISTER | 920 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EB102) | MODBUS_INPUT_REGISTER | 921 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EEV (EB101) | MODBUS_INPUT_REGISTER | 922 | 10 | °C | s16 | 0 | 0 | 0
Set point value EEV (EB102) | MODBUS_INPUT_REGISTER | 923 | 10 | °C | s16 | 0 | 0 | 0
EEV PV (EB102) | MODBUS_INPUT_REGISTER | 924 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EB102) | MODBUS_INPUT_REGISTER | 925 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EEV (EB102) | MODBUS_INPUT_REGISTER | 926 | 1 |  | u16 | 0 | 0 | 0
Superheat reference EVI (EB102) | MODBUS_INPUT_REGISTER | 927 | 10 | °C | s16 | 0 | 0 | 0
Superheat EVI (EB102) | MODBUS_INPUT_REGISTER | 928 | 10 | °C | s16 | 0 | 0 | 0
EEV-ssh-error (EVI)(EB102) | MODBUS_INPUT_REGISTER | 929 | 10 | °C | s16 | 0 | 0 | 0
Superheat temp. reference EVI (EB102) | MODBUS_INPUT_REGISTER | 930 | 10 | °C | s16 | 0 | 0 | 0
Set point value EVI (EB102) | MODBUS_INPUT_REGISTER | 931 | 10 | °C | s16 | 0 | 0 | 0
EVI PV (EB102) | MODBUS_INPUT_REGISTER | 932 | 10 | °C | s16 | 0 | 0 | 0
EEV-te-error average open (EVI)(EB102) | MODBUS_INPUT_REGISTER | 933 | 10 | °C | s16 | 0 | 0 | 0
Degree of opening EVI (EB102) | MODBUS_INPUT_REGISTER | 934 | 1 |  | u16 | 0 | 0 | 0
Smart energy source, priority select. in hot water | MODBUS_INPUT_REGISTER | 991 | 1 |  | u8 | 0 | 0 | 0
Outd. air heat pump, inverter, limits | MODBUS_INPUT_REGISTER | 992 | 1 |  | u8 | 0 | 0 | 0
Outd. air heat pump, inverter, speed reducing | MODBUS_INPUT_REGISTER | 993 | 1 |  | u8 | 0 | 0 | 0
Has one phase (EB101) | MODBUS_INPUT_REGISTER | 1008 | 1 |  | u8 | 0 | 0 | 0
Serial index (EB101) | MODBUS_INPUT_REGISTER | 1009 | 1 |  | u8 | 0 | 0 | 0
Limit DM | MODBUS_HOLDING_REGISTER | 18 | 10 | DM | s16 | -30000 | 30000 | 0
Calculated supply climate system 1 | MODBUS_INPUT_REGISTER | 1017 | 10 | °C | s16 | 0 | 0 | 0
Class 1 alarm | MODBUS_INPUT_REGISTER | 2195 | 1 |  | u8 | 0 | 0 | 0
Frost protection status | MODBUS_INPUT_REGISTER | 1018 | 1 |  | u16 | 0 | 0 | 0
Cooling status | MODBUS_INPUT_REGISTER | 1019 | 1 |  | u8 | 0 | 0 | 0
id:1726 | MODBUS_HOLDING_REGISTER | 2757 | 1 |  | s16 | 0 | 30000 | 0
Total run time additional heat | MODBUS_INPUT_REGISTER | 1025 | 10 | h | s32 | 0 | 1000000 | 0
Priority | MODBUS_INPUT_REGISTER | 1028 | 1 |  | u8 | 0 | 0 | 0
Operating mode internal add. heat | MODBUS_INPUT_REGISTER | 1029 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 4 | MODBUS_INPUT_REGISTER | 1030 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 3 | MODBUS_INPUT_REGISTER | 1031 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 2 | MODBUS_INPUT_REGISTER | 1032 | 1 |  | u8 | 0 | 0 | 0
Oper. mode shunt climate system 1 | MODBUS_INPUT_REGISTER | 1033 | 1 |  | u8 | 0 | 0 | 0
Operating. mode shunt controlled additional heat | MODBUS_INPUT_REGISTER | 1034 | 1 |  | u8 | 0 | 0 | 0
Fan mode 1 | MODBUS_INPUT_REGISTER | 1037 | 1 | % | u8 | 0 | 0 | 0
Current hot water mode | MODBUS_INPUT_REGISTER | 1038 | 1 |  | s8 | 0 | 0 | 0
Blocking cooling | MODBUS_INPUT_REGISTER | 1053 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 4 | MODBUS_INPUT_REGISTER | 1054 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 3 | MODBUS_INPUT_REGISTER | 1055 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 2 | MODBUS_INPUT_REGISTER | 1056 | 1 |  | u8 | 0 | 0 | 0
External adjustment climate system 1 | MODBUS_INPUT_REGISTER | 1057 | 1 |  | u8 | 0 | 0 | 0
External blocking | MODBUS_INPUT_REGISTER | 1058 | 1 |  | u8 | 0 | 0 | 0
Blocked | MODBUS_INPUT_REGISTER | 1059 | 1 |  | u8 | 0 | 0 | 0
External blocking, active cooling (HPAC) | MODBUS_INPUT_REGISTER | 1060 | 1 |  | u8 | 0 | 0 | 0
External blocking, passive cooling (HPAC) | MODBUS_INPUT_REGISTER | 1061 | 1 |  | u8 | 0 | 0 | 0
Step controlled add. heat blocking | MODBUS_INPUT_REGISTER | 1062 | 1 |  | u8 | 0 | 0 | 0
Hot water circulation (GP11) | MODBUS_INPUT_REGISTER | 1063 | 1 |  | u8 | 0 | 0 | 0
External heating medium pump (GP10) status | MODBUS_INPUT_REGISTER | 1066 | 1 |  | u8 | 0 | 0 | 0
Total HW run time additional heat | MODBUS_INPUT_REGISTER | 1069 | 10 | h | s32 | 0 | 9999999 | 0
More hot water status | MODBUS_INPUT_REGISTER | 1078 | 1 |  | u8 | 0 | 0 | 0
Relay status (HPAC) | MODBUS_INPUT_REGISTER | 1079 | 1 |  | u8 | 0 | 0 | 0
Holiday function status | MODBUS_HOLDING_REGISTER | 19 | 1 |  | s8 | 0 | 0 | 0
Docked compressors heating | MODBUS_INPUT_REGISTER | 1108 | 1 |  | u8 | 0 | 0 | 0
Docked compressors hot water | MODBUS_INPUT_REGISTER | 1109 | 1 |  | u8 | 0 | 0 | 0
Docked compressors pool 1 | MODBUS_INPUT_REGISTER | 1110 | 1 |  | u8 | 0 | 0 | 0
Reversing valve hot water (QN10) | MODBUS_INPUT_REGISTER | 2196 | 1 |  | u8 | 0 | 0 | 0
Relay status, base board (EB100-EP14) | MODBUS_INPUT_REGISTER | 1117 | 1 |  | u8 | 0 | 0 | 0
Relay status, imm. heat. board (EB100-EP14) | MODBUS_INPUT_REGISTER | 1119 | 1 |  | u16 | 0 | 0 | 0
Current status | MODBUS_INPUT_REGISTER | 1120 | 1 |  | u32 | 0 | 0 | 0
Functionality, heat pump (EP14) | MODBUS_INPUT_REGISTER | 1122 | 1 |  | u32 | 0 | 0 | 0
Active heat pumps | MODBUS_INPUT_REGISTER | 1124 | 1 |  | u16 | 0 | 0 | 0
Functionality, heat pump (EP15) | MODBUS_INPUT_REGISTER | 1125 | 1 |  | u32 | 0 | 0 | 0
Operating mode HW comfort | MODBUS_INPUT_REGISTER | 1129 | 1 |  | u8 | 0 | 0 | 0
Operating mode HW comfort additional heat | MODBUS_INPUT_REGISTER | 1130 | 1 |  | u8 | 0 | 0 | 0
Blocked | MODBUS_INPUT_REGISTER | 1131 | 1 |  | u8 | 0 | 0 | 0
Blocked | MODBUS_INPUT_REGISTER | 1132 | 1 |  | u8 | 0 | 0 | 0
Pool 2 (QN19) | MODBUS_INPUT_REGISTER | 1133 | 1 |  | u8 | 0 | 0 | 0
Pool 1 (QN19) | MODBUS_INPUT_REGISTER | 1134 | 1 |  | u8 | 0 | 0 | 0
Docked compressors pool 2 | MODBUS_INPUT_REGISTER | 1135 | 1 |  | u8 | 0 | 0 | 0
Version (EB101) | MODBUS_INPUT_REGISTER | 1451 | 1 |  | u16 | 0 | 0 | 0
Heat pump type (EB101) | MODBUS_INPUT_REGISTER | 1452 | 1 |  | u8 | 0 | 0 | 0
Compressor size (EB101) | MODBUS_INPUT_REGISTER | 1453 | 1 |  | u8 | 0 | 0 | 0
Return line (EB101-BT3) | MODBUS_INPUT_REGISTER | 1475 | 10 | °C | s16 | 0 | 0 | 0
Condenser sensor, supply line (EB101-BT12) | MODBUS_INPUT_REGISTER | 1478 | 10 | °C | s16 | 0 | 0 | 0
Discharge (EB101-BT14) | MODBUS_INPUT_REGISTER | 1479 | 10 | °C | s16 | 0 | 0 | 0
Liquid line (EB101-BT15) | MODBUS_INPUT_REGISTER | 1480 | 10 | °C | s16 | 0 | 0 | 0
Suction gas (EB101-BT17) | MODBUS_INPUT_REGISTER | 1481 | 10 | °C | s16 | 0 | 0 | 0
Compressor sensor (EB101-BT29) | MODBUS_INPUT_REGISTER | 1482 | 10 | °C | s16 | 0 | 0 | 0
Compressor status (EB101) | MODBUS_INPUT_REGISTER | 1484 | 1 |  | u8 | 0 | 0 | 0
Compressor, time to start (EB101-EP14) | MODBUS_INPUT_REGISTER | 1485 | 1 | min | u8 | 0 | 0 | 0
Relay status (EB101-EP14) | MODBUS_INPUT_REGISTER | 1486 | 1 |  | u16 | 0 | 0 | 0
Compressor, number of starts (EB101-EP14) | MODBUS_INPUT_REGISTER | 1489 | 1 |  | u32 | 0 | 2147483647 | 0
Compressor, oper. time, total (EB101-EP14) | MODBUS_INPUT_REGISTER | 1491 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, oper. time, hot water (EB101-EP14) | MODBUS_INPUT_REGISTER | 1493 | 1 | h | u32 | 0 | 2147483647 | 0
Alarm number (EB101-EP14) | MODBUS_INPUT_REGISTER | 1495 | 1 |  | u16 | 0 | 0 | 0
Version (EB100) | MODBUS_INPUT_REGISTER | 1496 | 1 |  | u16 | 0 | 0 | 0
Heat pump type (EB100) | MODBUS_INPUT_REGISTER | 1497 | 1 |  | u8 | 0 | 0 | 0
Compressor size (EB100) | MODBUS_INPUT_REGISTER | 1498 | 1 |  | u8 | 0 | 0 | 0
Compressor, oper. time, total (EB100-EP15) | MODBUS_INPUT_REGISTER | 1515 | 1 | h | u32 | 0 | 0 | 0
Compressor, oper. time, hot water (EB100-EP15) | MODBUS_INPUT_REGISTER | 1517 | 1 | h | u32 | 0 | 0 | 0
Return line (EB100-BT3) | MODBUS_INPUT_REGISTER | 1520 | 10 | °C | s16 | 0 | 0 | 0
Brine in (EB100-BT10) | MODBUS_INPUT_REGISTER | 1521 | 10 | °C | s16 | 0 | 0 | 0
Brine out (EB100-BT11) | MODBUS_INPUT_REGISTER | 1522 | 10 | °C | s16 | 0 | 0 | 0
Condenser (EB100-BT2) | MODBUS_INPUT_REGISTER | 1523 | 10 | °C | s16 | 0 | 0 | 0
Discharge (EB100-BT14) | MODBUS_INPUT_REGISTER | 1524 | 10 | °C | s16 | 0 | 0 | 0
Liquid line (EB100-BT15) | MODBUS_INPUT_REGISTER | 1525 | 10 | °C | s16 | 0 | 0 | 0
Suction gas (EB100-BT17) | MODBUS_INPUT_REGISTER | 1526 | 10 | °C | s16 | 0 | 0 | 0
Compressor sensor (EB100-BT29) | MODBUS_INPUT_REGISTER | 1527 | 10 | °C | s16 | 0 | 0 | 0
Low press (EB100-BP8) | MODBUS_INPUT_REGISTER | 1528 | 10 | °C | s16 | 0 | 0 | 0
Compressor status (EB100) | MODBUS_INPUT_REGISTER | 1529 | 1 |  | u8 | 0 | 0 | 0
Compressor, time to start (EB100-EP14) | MODBUS_INPUT_REGISTER | 1530 | 1 | min | u8 | 0 | 0 | 0
Relay status (EB100-EP14) | MODBUS_INPUT_REGISTER | 1531 | 1 |  | u16 | 0 | 0 | 0
Heating medium pump (EB100) | MODBUS_INPUT_REGISTER | 1532 | 1 | % | u8 | 0 | 0 | 0
Brine pump (EB100) | MODBUS_INPUT_REGISTER | 1533 | 1 | % | u8 | 0 | 0 | 0
Compressor, number of starts (EB100-EP14) | MODBUS_INPUT_REGISTER | 1534 | 1 |  | u32 | 0 | 0 | 0
Compressor, oper. time, total (EB100-EP14) | MODBUS_INPUT_REGISTER | 1536 | 1 | h | u32 | 0 | 0 | 0
Compressor, oper. time, hot water (EB100-EP14) | MODBUS_INPUT_REGISTER | 1538 | 1 | h | u32 | 0 | 0 | 0
Compressor, requested (EB108-EP15) | MODBUS_INPUT_REGISTER | 1541 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB108-EP14) | MODBUS_INPUT_REGISTER | 1542 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB107-EP15) | MODBUS_INPUT_REGISTER | 1543 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB107-EP14) | MODBUS_INPUT_REGISTER | 1544 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB106-EP15) | MODBUS_INPUT_REGISTER | 1545 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB106-EP14) | MODBUS_INPUT_REGISTER | 1546 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB105-EP15) | MODBUS_INPUT_REGISTER | 1547 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB105-EP14) | MODBUS_INPUT_REGISTER | 1548 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB104-EP15) | MODBUS_INPUT_REGISTER | 1549 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB104-EP14) | MODBUS_INPUT_REGISTER | 1550 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB103-EP15) | MODBUS_INPUT_REGISTER | 1551 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB103-EP14) | MODBUS_INPUT_REGISTER | 1552 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB102-EP15) | MODBUS_INPUT_REGISTER | 1553 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB102-EP14) | MODBUS_INPUT_REGISTER | 1554 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB101-EP15) | MODBUS_INPUT_REGISTER | 1555 | 1 |  | u8 | 0 | 0 | 0
Compressor, requested (EB101-EP14) | MODBUS_INPUT_REGISTER | 1556 | 1 |  | u8 | 0 | 0 | 0
Cooling blocking | MODBUS_INPUT_REGISTER | 1559 | 1 |  | u8 | 0 | 0 | 0
Date, periodic hot water | MODBUS_INPUT_REGISTER | 1561 | 1 |  | -
Blocked compressors | MODBUS_INPUT_REGISTER | 2174 | 1 |  | u32 | 0 | 0 | 0
Cooling degree minutes | MODBUS_HOLDING_REGISTER | 20 | 10 | DM | s16 | -30000 | 30000 | 0
Status (ACS) | MODBUS_INPUT_REGISTER | 1568 | 1 |  | u8 | 0 | 0 | 0
Status, heating dumping (ACS) | MODBUS_INPUT_REGISTER | 1569 | 1 |  | u8 | 0 | 0 | 0
Status, cooling dumping (ACS) | MODBUS_INPUT_REGISTER | 1570 | 1 |  | u8 | 0 | 0 | 0
Used compressors hot water | MODBUS_INPUT_REGISTER | 1571 | 1 |  | u8 | 0 | 0 | 0
Used compressors heating | MODBUS_INPUT_REGISTER | 1572 | 1 |  | u8 | 0 | 0 | 0
Used compressors pool 1 | MODBUS_INPUT_REGISTER | 1573 | 1 |  | u8 | 0 | 0 | 0
Used compressors pool 2 | MODBUS_INPUT_REGISTER | 1574 | 1 |  | u8 | 0 | 0 | 0
id:2728 | MODBUS_HOLDING_REGISTER | 3099 | 1 |  | s32 | 0 | 9999999 | 0
Used compressors cooling | MODBUS_INPUT_REGISTER | 1588 | 1 |  | u8 | 0 | 0 | 0
Outdoor temperature (EB101-BT28) | MODBUS_INPUT_REGISTER | 1621 | 10 | °C | s16 | 0 | 0 | 0
Evaporator (EB101-BT16) | MODBUS_INPUT_REGISTER | 1622 | 10 | °C | s16 | 0 | 0 | 0
(EB100-EP15-BT28) | MODBUS_INPUT_REGISTER | 1623 | 10 | °C | s16 | 0 | 0 | 0
(EB100-EP15-BT16) | MODBUS_INPUT_REGISTER | 1624 | 10 | °C | s16 | 0 | 0 | 0
(EB100-EP14-BT28) | MODBUS_INPUT_REGISTER | 1625 | 10 | °C | s16 | 0 | 0 | 0
(EB100-EP14-BT16) | MODBUS_INPUT_REGISTER | 1626 | 10 | °C | s16 | 0 | 0 | 0
Charge pump speed (EB101-GP12) | MODBUS_INPUT_REGISTER | 1636 | 1 | % | u8 | 0 | 0 | 0
Frost protection heat exchanger heat pump 1 | MODBUS_INPUT_REGISTER | 1638 | 1 |  | u8 | 0 | 0 | 0
Bit register (EB100) | MODBUS_INPUT_REGISTER | 1687 | 1 |  | u8 | 0 | 0 | 0
Controlling hot water sensor (EB100-BT6) | MODBUS_INPUT_REGISTER | 1688 | 10 | °C | s16 | 0 | 0 | 0
Display hot water sensor (EB100-BT7) | MODBUS_INPUT_REGISTER | 1689 | 10 | °C | s16 | 0 | 0 | 0
Supply temperature sensor (EB100-BT2) | MODBUS_INPUT_REGISTER | 1690 | 10 | °C | s16 | 0 | 0 | 0
Compressor status (EB100-EP15) | MODBUS_INPUT_REGISTER | 1691 | 1 |  | u8 | 0 | 0 | 0
Compressor status (EB100-EP14) | MODBUS_INPUT_REGISTER | 1692 | 1 |  | u8 | 0 | 0 | 0
Operating mode extra additional heat | MODBUS_INPUT_REGISTER | 1693 | 1 |  | u8 | 0 | 0 | 0
Docked compressors cooling | MODBUS_INPUT_REGISTER | 1694 | 1 |  | u8 | 0 | 0 | 0
BP4, unprocessed (EB108-EP15) | MODBUS_INPUT_REGISTER | 1695 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB108-EP15--BP8) | MODBUS_INPUT_REGISTER | 1697 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB108-EP15) | MODBUS_INPUT_REGISTER | 1699 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB108-EP15) | MODBUS_INPUT_REGISTER | 1700 | 1 |  | u8 | 0 | 0 | 0
BP4, unprocessed (EB108-EP14) | MODBUS_INPUT_REGISTER | 1702 | 1 |  | s16 | 0 | 0 | 0
Defrosting (EB108) | MODBUS_INPUT_REGISTER | 1707 | 1 |  | u8 | 0 | 0 | 0
BP4, unprocessed (EB107-EP15) | MODBUS_INPUT_REGISTER | 1709 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB107-EP15--BP8) | MODBUS_INPUT_REGISTER | 1711 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB107-EP15) | MODBUS_INPUT_REGISTER | 1713 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB107-EP15) | MODBUS_INPUT_REGISTER | 1714 | 1 |  | u8 | 0 | 0 | 0
Power (EB107-EP15) | MODBUS_INPUT_REGISTER | 1715 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB107-EP14) | MODBUS_INPUT_REGISTER | 1716 | 1 |  | s16 | 0 | 0 | 0
Defrosting (EB107) | MODBUS_INPUT_REGISTER | 1721 | 1 |  | u8 | 0 | 0 | 0
Power (EB107-EP14) | MODBUS_INPUT_REGISTER | 1722 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB106-EP15) | MODBUS_INPUT_REGISTER | 1723 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB106-EP15--BP8) | MODBUS_INPUT_REGISTER | 1725 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB106-EP15) | MODBUS_INPUT_REGISTER | 1727 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB106-EP15) | MODBUS_INPUT_REGISTER | 1728 | 1 |  | u8 | 0 | 0 | 0
Power (EB106-EP15) | MODBUS_INPUT_REGISTER | 1729 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB106-EP14) | MODBUS_INPUT_REGISTER | 1730 | 1 |  | s16 | 0 | 0 | 0
Defrosting (EB106) | MODBUS_INPUT_REGISTER | 1735 | 1 |  | u8 | 0 | 0 | 0
Power (EB106-EP14) | MODBUS_INPUT_REGISTER | 1736 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB105-EP15) | MODBUS_INPUT_REGISTER | 1737 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB105-EP15--BP8) | MODBUS_INPUT_REGISTER | 1739 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB105-EP15) | MODBUS_INPUT_REGISTER | 1741 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB105-EP15) | MODBUS_INPUT_REGISTER | 1742 | 1 |  | u8 | 0 | 0 | 0
Power (EB105-EP15) | MODBUS_INPUT_REGISTER | 1743 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB105-EP14) | MODBUS_INPUT_REGISTER | 1744 | 1 |  | s16 | 0 | 0 | 0
Defrosting (EB105) | MODBUS_INPUT_REGISTER | 1749 | 1 |  | u8 | 0 | 0 | 0
Power (EB105-EP15) | MODBUS_INPUT_REGISTER | 1750 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB104-EP15) | MODBUS_INPUT_REGISTER | 1751 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB104-EP15--BP8) | MODBUS_INPUT_REGISTER | 1753 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB104-EP15) | MODBUS_INPUT_REGISTER | 1755 | 1 |  | u16 | 0 | 0 | 0
Low pressure (EB103-EP15--BP8) | MODBUS_INPUT_REGISTER | 1767 | 10 | bar | s16 | 0 | 0 | 0
BP4, unprocessed (EB103-EP14) | MODBUS_INPUT_REGISTER | 1772 | 1 |  | s16 | 0 | 0 | 0
Defrosting (EB103) | MODBUS_INPUT_REGISTER | 1777 | 1 |  | u8 | 0 | 0 | 0
Power (EB103-EP14) | MODBUS_INPUT_REGISTER | 1778 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB102-EP15) | MODBUS_INPUT_REGISTER | 1779 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB102-EP15--BP8) | MODBUS_INPUT_REGISTER | 1781 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB102-EP15) | MODBUS_INPUT_REGISTER | 1783 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB102-EP15) | MODBUS_INPUT_REGISTER | 1784 | 1 |  | u8 | 0 | 0 | 0
Power (EB102-EP15) | MODBUS_INPUT_REGISTER | 1785 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB102-EP14) | MODBUS_INPUT_REGISTER | 1786 | 1 |  | s16 | 0 | 0 | 0
Defrosting (EB102) | MODBUS_INPUT_REGISTER | 1791 | 1 |  | u8 | 0 | 0 | 0
Power (EB102-EP14) | MODBUS_INPUT_REGISTER | 1792 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB101-EP15) | MODBUS_INPUT_REGISTER | 1793 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB101-EP15-BP8) | MODBUS_INPUT_REGISTER | 1795 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB101-EP15) | MODBUS_INPUT_REGISTER | 1797 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB101-EP15) | MODBUS_INPUT_REGISTER | 1798 | 1 |  | u8 | 0 | 0 | 0
Power (EB101-EP15) | MODBUS_INPUT_REGISTER | 1799 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB101-EP14) | MODBUS_INPUT_REGISTER | 1800 | 1 |  | s16 | 0 | 0 | 0
Low pressure (EB101-BP8) | MODBUS_INPUT_REGISTER | 1802 | 10 | bar | s16 | 0 | 0 | 0
Current compressor frequency (EB101) | MODBUS_INPUT_REGISTER | 1803 | 10 | Hz | s16 | 0 | 0 | 0
Protection mode (EB101) | MODBUS_INPUT_REGISTER | 1804 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB101) | MODBUS_INPUT_REGISTER | 1805 | 1 |  | u8 | 0 | 0 | 0
Power (EB101-EP14) | MODBUS_INPUT_REGISTER | 1806 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB100-EP15) | MODBUS_INPUT_REGISTER | 1807 | 1 |  | s16 | 0 | 0 | 0
Pressure sensor, condenser (EB100-EP15-BP4) | MODBUS_INPUT_REGISTER | 1808 | 10 | bar | s16 | 0 | 0 | 0
Low pressure (EB100-EP15-BP8) | MODBUS_INPUT_REGISTER | 1809 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB100-EP15) | MODBUS_INPUT_REGISTER | 1811 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB100-EP15) | MODBUS_INPUT_REGISTER | 1812 | 1 |  | u8 | 0 | 0 | 0
Power (EB100-EP15) | MODBUS_INPUT_REGISTER | 1813 | 1 | kW | u8 | 0 | 0 | 0
BP4, unprocessed (EB100-EP14) | MODBUS_INPUT_REGISTER | 1814 | 1 |  | s16 | 0 | 0 | 0
Pressure sensor, condenser (EB100-EP14-BP4) | MODBUS_INPUT_REGISTER | 1815 | 10 | bar | s16 | 0 | 0 | 0
Low pressure (EB100-EP14-BP8) | MODBUS_INPUT_REGISTER | 1816 | 10 | bar | s16 | 0 | 0 | 0
Prot. status (EB100-EP14) | MODBUS_INPUT_REGISTER | 1818 | 1 |  | u16 | 0 | 0 | 0
Defrosting (EB100-EP14) | MODBUS_INPUT_REGISTER | 1819 | 1 |  | u8 | 0 | 0 | 0
Power (EB100-EP14) | MODBUS_INPUT_REGISTER | 1820 | 1 | kW | u8 | 0 | 0 | 0
Climate system 4 | MODBUS_INPUT_REGISTER | 1823 | 1 |  | u8 | 0 | 0 | 0
Climate system 3 | MODBUS_INPUT_REGISTER | 1824 | 1 |  | u8 | 0 | 0 | 0
Climate system 2 | MODBUS_INPUT_REGISTER | 1825 | 1 |  | u8 | 0 | 0 | 0
Climate system 1 (HMP) | MODBUS_INPUT_REGISTER | 1826 | 1 |  | u8 | 0 | 0 | 0
Pool 2 pump status | MODBUS_INPUT_REGISTER | 1827 | 1 |  | u8 | 0 | 0 | 0
Pool 1 pump status | MODBUS_INPUT_REGISTER | 1828 | 1 |  | u8 | 0 | 0 | 0
ACS EQ1-QN12 | MODBUS_INPUT_REGISTER | 1830 | 1 |  | u8 | 0 | 0 | 0
ACS EQ1-GP20 | MODBUS_INPUT_REGISTER | 1831 | 1 |  | u8 | 0 | 0 | 0
Passive cooling pump (GP13) | MODBUS_INPUT_REGISTER | 1833 | 1 |  | u8 | 0 | 0 | 0
Oper. mode groundwater pump | MODBUS_INPUT_REGISTER | 1835 | 1 |  | u8 | 0 | 0 | 0
Alarm number (EB100-EP15) | MODBUS_INPUT_REGISTER | 1837 | 1 |  | u16 | 0 | 0 | 0
Alarm number (EB100-EP14) | MODBUS_INPUT_REGISTER | 1838 | 1 |  | u16 | 0 | 0 | 0
Requested compressor frequency (EB108-EP15) | MODBUS_INPUT_REGISTER | 1839 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB107-EP15) | MODBUS_INPUT_REGISTER | 1841 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB106-EP15) | MODBUS_INPUT_REGISTER | 1843 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB105-EP15) | MODBUS_INPUT_REGISTER | 1845 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB104-EP15) | MODBUS_INPUT_REGISTER | 1847 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB103-EP15) | MODBUS_INPUT_REGISTER | 1849 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB102-EP15) | MODBUS_INPUT_REGISTER | 1851 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB101-EP15) | MODBUS_INPUT_REGISTER | 1853 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EB101) | MODBUS_INPUT_REGISTER | 1854 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency (EP15) | MODBUS_INPUT_REGISTER | 1855 | 1 | Hz | u8 | 0 | 0 | 0
Requested compressor frequency | MODBUS_INPUT_REGISTER | 1856 | 1 | Hz | u8 | 0 | 0 | 0
Operating mode, shunt controlled brine (QN41) | MODBUS_INPUT_REGISTER | 2410 | 1 |  | u8 | 0 | 0 | 0
Low press. sensor, unprocessed (EB101-EP14) | MODBUS_INPUT_REGISTER | 1902 | 1 |  | s16 | 0 | 0 | 0
Current sensor (EB101-EP14) | MODBUS_INPUT_REGISTER | 1903 | 10 | A | s16 | 0 | 0 | 0
Low press. sensor, unprocessed (EB100-EP15) | MODBUS_INPUT_REGISTER | 1905 | 1 |  | s16 | 0 | 0 | 0
Current sensor (EB100-EP15) | MODBUS_INPUT_REGISTER | 1906 | 10 | A | s16 | 0 | 0 | 0
Low press. sensor, unprocessed (EB100-EP14) | MODBUS_INPUT_REGISTER | 1908 | 1 |  | s16 | 0 | 0 | 0
Current sensor (EB100-EP14) | MODBUS_INPUT_REGISTER | 1909 | 10 | A | s16 | 0 | 0 | 0
Operating mode (SG Ready) | MODBUS_INPUT_REGISTER | 1911 | 1 |  | u8 | 0 | 0 | 0
SG ready, input A | MODBUS_INPUT_REGISTER | 1912 | 1 |  | u8 | 0 | 0 | 0
SG ready, input B | MODBUS_INPUT_REGISTER | 1913 | 1 |  | u8 | 0 | 0 | 0
Hot water comfort mode (SPA) | MODBUS_INPUT_REGISTER | 1915 | 1 |  | s8 | 0 | 0 | 0
Pool offset (SPA) | MODBUS_INPUT_REGISTER | 1916 | 1 |  | s8 | 0 | 0 | 0
Cooling offset (SPA) | MODBUS_INPUT_REGISTER | 1917 | 1 |  | s8 | 0 | 0 | 0
Operating mode (Smart Price Adaption) | MODBUS_INPUT_REGISTER | 1918 | 1 |  | u8 | 0 | 0 | 0
Evaporator 2 (EB101-EP14-BT16) | MODBUS_INPUT_REGISTER | 1966 | 10 | °C | s16 | 0 | 0 | 0
Temperature, inverter (EB101-EP14) | MODBUS_INPUT_REGISTER | 1967 | 10 | °C | s16 | 0 | 0 | 0
fan speed (EB101-EP14) | MODBUS_INPUT_REGISTER | 1968 | 1 |  | u8 | 0 | 0 | 0
Evaporator 2 (EB100-EP15-BT16) | MODBUS_INPUT_REGISTER | 1969 | 10 | °C | s16 | 0 | 0 | 0
Temperature, inverter (EB100-EP15) | MODBUS_INPUT_REGISTER | 1970 | 10 | °C | s16 | 0 | 0 | 0
fan speed (EB100-EP15) | MODBUS_INPUT_REGISTER | 1971 | 1 |  | u8 | 0 | 0 | 0
Evaporator 2 (EB100-EP14-BT16) | MODBUS_INPUT_REGISTER | 1972 | 10 | °C | s16 | 0 | 0 | 0
Temperature, inverter (EB100-EP14) | MODBUS_INPUT_REGISTER | 1973 | 10 | °C | s16 | 0 | 0 | 0
fan speed (EB100-EP14) | MODBUS_INPUT_REGISTER | 1974 | 1 |  | u8 | 0 | 0 | 0
Alarm number | MODBUS_INPUT_REGISTER | 1975 | 1 |  | s16 | 0 | 0 | 0
Reset alarm | MODBUS_HOLDING_REGISTER | 22 | 1 |  | u8 | 0 | 0 | 0
Non module-specific alarm numbers | MODBUS_INPUT_REGISTER | 1976 | 1 |  | s16 | 0 | 0 | 0
Heating curve climate system 1 | MODBUS_HOLDING_REGISTER | 26 | 1 |  | s8 | 0 | 15 | 9
Heating offset climate system 1 | MODBUS_HOLDING_REGISTER | 30 | 1 |  | s8 | -10 | 10 | 0
Min supply climate system 1 | MODBUS_HOLDING_REGISTER | 34 | 10 | °C | s16 | 50 | 800 | 200
Max supply climate system 1 | MODBUS_HOLDING_REGISTER | 38 | 10 | °C | s16 | 50 | 800 | 600
Own curve, heating P7 | MODBUS_HOLDING_REGISTER | 39 | 1 | °C | s8 | 5 | 80 | 15
Own curve, heating P6 | MODBUS_HOLDING_REGISTER | 40 | 1 | °C | s8 | 5 | 80 | 15
Own curve, heating P5 | MODBUS_HOLDING_REGISTER | 41 | 1 | °C | s8 | 5 | 80 | 26
Own curve, heating P4 | MODBUS_HOLDING_REGISTER | 42 | 1 | °C | s8 | 5 | 80 | 32
Own curve, heating P3 | MODBUS_HOLDING_REGISTER | 43 | 1 | °C | s8 | 5 | 80 | 35
Own curve, heating P2 | MODBUS_HOLDING_REGISTER | 44 | 1 | °C | s8 | 5 | 80 | 40
Own curve, heating P1 | MODBUS_HOLDING_REGISTER | 45 | 1 | °C | s8 | 5 | 80 | 45
Point offset outdoor temperature | MODBUS_HOLDING_REGISTER | 46 | 1 | °C | s8 | -40 | 30 | 0
Point offset | MODBUS_HOLDING_REGISTER | 47 | 1 | °C | s8 | -10 | 10 | 0
External adjustment climate system 1 | MODBUS_HOLDING_REGISTER | 51 | 1 |  | s8 | -10 | 10 | 0
External adjustment with room sensor climate system 1 | MODBUS_HOLDING_REGISTER | 55 | 10 | °C | s16 | 50 | 300 | 200
Stop temperature HW periodic increase | MODBUS_HOLDING_REGISTER | 61 | 10 | °C | s16 | 550 | 700 | 550
Periodic hot water | MODBUS_HOLDING_REGISTER | 65 | 1 |  | s8 | 0 | 1 | 1
Periodic hot water interval | MODBUS_HOLDING_REGISTER | 66 | 1 | days | s8 | 1 | 90 | 7
Start time periodic hot water | MODBUS_HOLDING_REGISTER | 67 | 1 |  | -
Language | MODBUS_HOLDING_REGISTER | 91 | 1 |  | s8 | 0 | 24 | 0
Operating mode | MODBUS_HOLDING_REGISTER | 2743 | 1 |  | u8 | 0 | 2 | 0
Operating mode heating medium pump | MODBUS_HOLDING_REGISTER | 95 | 1 |  | u8 | 10 | 40 | 40
Activate forced control | MODBUS_HOLDING_REGISTER | 5000 | 1 |  | u8 | 0 | 0 | 0
Fuse | MODBUS_HOLDING_REGISTER | 103 | 1 | A | u16 | 1 | 400 | 32
Phase Order L3 | MODBUS_HOLDING_REGISTER | 2747 | 1 |  | u8 | 1 | 128 | 4
Phase Order L2 | MODBUS_HOLDING_REGISTER | 2746 | 1 |  | u8 | 1 | 128 | 2
Phase Order L1 | MODBUS_HOLDING_REGISTER | 2745 | 1 |  | u8 | 1 | 128 | 1
Floor drying | MODBUS_HOLDING_REGISTER | 120 | 1 |  | u8 | 0 | 1 | 0
Floor drying period 7 | MODBUS_HOLDING_REGISTER | 121 | 1 | days | u8 | 0 | 30 | 2
Floor drying period 6 | MODBUS_HOLDING_REGISTER | 122 | 1 | days | u8 | 0 | 30 | 2
Floor drying period 5 | MODBUS_HOLDING_REGISTER | 123 | 1 | days | u8 | 0 | 30 | 2
Floor drying period 4 | MODBUS_HOLDING_REGISTER | 124 | 1 | days | u8 | 0 | 30 | 3
Floor drying period 3 | MODBUS_HOLDING_REGISTER | 125 | 1 | days | u8 | 0 | 30 | 2
Floor drying period 2 | MODBUS_HOLDING_REGISTER | 126 | 1 | days | u8 | 0 | 30 | 2
Floor drying period 1 | MODBUS_HOLDING_REGISTER | 127 | 1 | days | u8 | 0 | 30 | 2
Floor drying temp. 7 | MODBUS_HOLDING_REGISTER | 128 | 1 | °C | u8 | 15 | 70 | 20
Floor drying temp. 6 | MODBUS_HOLDING_REGISTER | 129 | 1 | °C | u8 | 15 | 70 | 30
Floor drying temp. 5 | MODBUS_HOLDING_REGISTER | 130 | 1 | °C | u8 | 15 | 70 | 40
Floor drying temp. 4 | MODBUS_HOLDING_REGISTER | 131 | 1 | °C | u8 | 15 | 70 | 45
Floor drying temp. 3 | MODBUS_HOLDING_REGISTER | 132 | 1 | °C | u8 | 15 | 70 | 40
Floor drying temp. 2 | MODBUS_HOLDING_REGISTER | 133 | 1 | °C | u8 | 15 | 70 | 30
Floor drying temp. 1 | MODBUS_HOLDING_REGISTER | 134 | 1 | °C | u8 | 15 | 70 | 20
Floor drying ongoing time. | MODBUS_INPUT_REGISTER | 1977 | 1 |  | u16 | 0 | 10000 | 0
Dimensioned outdoor temperature | MODBUS_HOLDING_REGISTER | 140 | 10 | °C | s16 | -400 | 200 | -180
Delta T for DOT | MODBUS_HOLDING_REGISTER | 141 | 10 | °C | s16 | 10 | 250 | 100
Climate system 2 | MODBUS_HOLDING_REGISTER | 142 | 1 |  | u8 | 0 | 1 | 0
Climate system 3 | MODBUS_HOLDING_REGISTER | 143 | 1 |  | u8 | 0 | 1 | 0
Climate system 4 | MODBUS_HOLDING_REGISTER | 144 | 1 |  | u8 | 0 | 1 | 0
Shunt controlled additional heat | MODBUS_HOLDING_REGISTER | 153 | 1 |  | u8 | 0 | 1 | 0
Wait time shunt, shunt controlled additional heat | MODBUS_HOLDING_REGISTER | 157 | 1 | s | s16 | 10 | 300 | 30
Step controlled additional heat accessory | MODBUS_HOLDING_REGISTER | 158 | 1 |  | u8 | 0 | 1 | 0
Ground water pump accessory | MODBUS_HOLDING_REGISTER | 162 | 1 |  | u8 | 0 | 1 | 0
Waiting time cooling/heating | MODBUS_HOLDING_REGISTER | 165 | 1 | h | s8 | 0 | 48 | 2
Heating start at under temp. | MODBUS_HOLDING_REGISTER | 166 | 10 | °C | s8 | 5 | 100 | 10
Cooling start at over temp. | MODBUS_HOLDING_REGISTER | 167 | 10 | °C | s8 | 5 | 100 | 30
Cooling shunt amplification | MODBUS_HOLDING_REGISTER | 168 | 10 |  | s8 | 1 | 100 | 10
Cooling shunt waiting time | MODBUS_HOLDING_REGISTER | 169 | 1 | s | s16 | 10 | 300 | 30
Cooling with room sensors | MODBUS_HOLDING_REGISTER | 170 | 10 |  | u8 | 0 | 41 | 0
Start passive cooling DM | MODBUS_HOLDING_REGISTER | 172 | 1 | DM | s16 | 10 | 500 | 30
Start active cooling DM | MODBUS_HOLDING_REGISTER | 173 | 1 | DM | s16 | 10 | 300 | 30
Changes have been made | MODBUS_HOLDING_REGISTER | 2744 | 1 |  | u8 | 0 | 1 | 0
Permit additional heat, heating | MODBUS_HOLDING_REGISTER | 180 | 1 |  | u8 | 0 | 1 | 1
Permit heating | MODBUS_HOLDING_REGISTER | 181 | 1 |  | u8 | 0 | 1 | 1
Permit cooling | MODBUS_HOLDING_REGISTER | 182 | 1 |  | u8 | 0 | 1 | 1
Auto mode, stop temperature for heating | MODBUS_HOLDING_REGISTER | 184 | 10 | °C | s16 | -200 | 400 | 170
Auto mode, additional heat stop temperature | MODBUS_HOLDING_REGISTER | 185 | 10 | °C | s16 | -250 | 400 | 50
Auto mode filter time | MODBUS_HOLDING_REGISTER | 186 | 1 | h | u8 | 0 | 48 | 24
Max difference supply, compressor | MODBUS_HOLDING_REGISTER | 187 | 10 | °C | s16 | 10 | 250 | 100
Max difference supply, additional heat | MODBUS_HOLDING_REGISTER | 188 | 10 | °C | s16 | 10 | 240 | 70
Time format | MODBUS_HOLDING_REGISTER | 194 | 1 |  | u8 | 0 | 1 | 1
Hot water permitted | MODBUS_HOLDING_REGISTER | 195 | 1 |  | u8 | 0 | 1 | 0
Alarm action, lower room temperature | MODBUS_HOLDING_REGISTER | 196 | 1 |  | u8 | 0 | 1 | 0
Auxiliary operation on alarm | MODBUS_HOLDING_REGISTER | 198 | 1 |  | u8 | 0 | 0 | 0
Use room sensor climate system 4 | MODBUS_HOLDING_REGISTER | 199 | 1 |  | u8 | 0 | 1 | 0
Use room sensor climate system 3 | MODBUS_HOLDING_REGISTER | 200 | 1 |  | u8 | 0 | 1 | 0
Use room sensor climate system 2 | MODBUS_HOLDING_REGISTER | 201 | 1 |  | u8 | 0 | 1 | 0
Use room sensor climate system 1 | MODBUS_HOLDING_REGISTER | 202 | 1 |  | u8 | 0 | 1 | 0
Room sensor set point value climate system 4 | MODBUS_HOLDING_REGISTER | 203 | 10 | °C | s16 | 50 | 300 | 200
Room sensor set point value climate system 3 | MODBUS_HOLDING_REGISTER | 204 | 10 | °C | s16 | 50 | 300 | 200
Room sensor set point value climate system 2 | MODBUS_HOLDING_REGISTER | 205 | 10 | °C | s16 | 50 | 300 | 200
Room sensor set point value climate system 1 | MODBUS_HOLDING_REGISTER | 206 | 10 | °C | s16 | 50 | 300 | 200
Room sensor factor climate system 4 | MODBUS_HOLDING_REGISTER | 207 | 10 |  | u8 | 0 | 60 | 20
Room sensor factor climate system 3 | MODBUS_HOLDING_REGISTER | 208 | 10 |  | u8 | 0 | 60 | 20
Room sensor factor climate system 2 | MODBUS_HOLDING_REGISTER | 209 | 10 |  | u8 | 0 | 60 | 20
Room sensor factor climate system 1 | MODBUS_HOLDING_REGISTER | 210 | 10 |  | u8 | 0 | 60 | 20
Input AUX5 | MODBUS_HOLDING_REGISTER | 211 | 1 |  | u8 | 0 | 68 | 0
Input AUX4 | MODBUS_HOLDING_REGISTER | 212 | 1 |  | u8 | 0 | 68 | 0
Input AUX3 | MODBUS_HOLDING_REGISTER | 213 | 1 |  | u8 | 0 | 68 | 0
Input AUX2 | MODBUS_HOLDING_REGISTER | 214 | 1 |  | u8 | 0 | 68 | 0
Input AUX1 | MODBUS_HOLDING_REGISTER | 215 | 1 |  | u8 | 0 | 68 | 0
Output AUX1 | MODBUS_HOLDING_REGISTER | 216 | 1 |  | u8 | 0 | 30 | 0
Speed, brine pump | MODBUS_HOLDING_REGISTER | 222 | 1 | % | u8 | 1 | 100 | 100
id:3968 | MODBUS_HOLDING_REGISTER | 2752 | 1 |  | u16 | 1 | 3600 | 5
Preset flow setting for climate system | MODBUS_HOLDING_REGISTER | 223 | 1 |  | u8 | 0 | 3 | 1
id:3977 | MODBUS_HOLDING_REGISTER | 2753 | 1 |  | u8 | 21 | 22 | 21
More hot water (Number of minutes) | MODBUS_HOLDING_REGISTER | 225 | 1 |  | u16 | 0 | 0 | 0
id:4045 | MODBUS_HOLDING_REGISTER | 5245 | 1 | °C | s8 | 1 | 40 | 8
id:4046 | MODBUS_HOLDING_REGISTER | 5247 | 1 | °C | s8 | 0 | 40 | 4
id:4049 | MODBUS_HOLDING_REGISTER | 5249 | 1 |  | u8 | 0 | 1 | 0
id:4050 | MODBUS_HOLDING_REGISTER | 5250 | 1 |  | u8 | 0 | 1 | 0
id:4051 | MODBUS_HOLDING_REGISTER | 5251 | 1 |  | u8 | 0 | 1 | 0
Oper. mode | MODBUS_HOLDING_REGISTER | 237 | 1 |  | u8 | 0 | 0 | 0
Max. step internal additional heat | MODBUS_HOLDING_REGISTER | 238 | 1 |  | u8 | 0 | 7 | 3
Internal additional heat stepping mode | MODBUS_HOLDING_REGISTER | 239 | 1 |  | u8 | 0 | 1 | 0
Cooling heat sensor set point value | MODBUS_HOLDING_REGISTER | 681 | 10 |  | s16 | 50 | 400 | 210
Heating medium pump manual speed | MODBUS_HOLDING_REGISTER | 682 | 1 | % | s8 | 1 | 100 | 70
Pool 2 accessory | MODBUS_HOLDING_REGISTER | 684 | 1 |  | u8 | 0 | 1 | 0
Pool 1 accessory | MODBUS_HOLDING_REGISTER | 685 | 1 |  | u8 | 0 | 1 | 0
Hot water comfort | MODBUS_HOLDING_REGISTER | 694 | 1 |  | u8 | 0 | 1 | 0
Manual heating medium pump speed | MODBUS_HOLDING_REGISTER | 695 | 1 | % | s8 | 0 | 1 | 0
More hot water | MODBUS_HOLDING_REGISTER | 697 | 1 |  | s8 | 0 | 0 | 0
Start diff. DM, step-controlled add. heat | MODBUS_HOLDING_REGISTER | 703 | 1 | DM | s16 | 0 | 2000 | 400
HW comfort shunt on/off | MODBUS_HOLDING_REGISTER | 705 | 1 |  | u8 | 0 | 1 | 0
External cooling accessory | MODBUS_HOLDING_REGISTER | 709 | 1 |  | u8 | 0 | 1 | 0
HW comfort additional heat | MODBUS_HOLDING_REGISTER | 710 | 1 |  | u8 | 0 | 1 | 0
id:4591 | MODBUS_HOLDING_REGISTER | 5256 | 1 |  | s8 | 5 | 80 | 30
Cooling connected, climate system 1 | MODBUS_HOLDING_REGISTER | 726 | 1 |  | u8 | 0 | 1 | 1
ACS | MODBUS_HOLDING_REGISTER | 731 | 1 |  | u8 | 0 | 1 | 0
id:4617 | MODBUS_HOLDING_REGISTER | 5257 | 1 |  | s8 | 0 | 1 | 0
Op. mode charge pump (EB101) | MODBUS_HOLDING_REGISTER | 748 | 1 |  | u8 | 0 | 1 | 0
id:4660 | MODBUS_HOLDING_REGISTER | 5267 | 1 |  | u8 | 0 | 0 | 0
Shunted brine, accessory | MODBUS_HOLDING_REGISTER | 5268 | 1 |  | u8 | 0 | 1 | 0
Shunted brine max. temp. | MODBUS_HOLDING_REGISTER | 5271 | 1 | °C | u8 | 0 | 30 | 20
Hot water compressors step diff. | MODBUS_HOLDING_REGISTER | 755 | 100 |  | s16 | 0 | 400 | 100
Additional heat after reversing valve | MODBUS_HOLDING_REGISTER | 758 | 1 |  | u8 | 0 | 1 | 1
Heating (SG Ready) | MODBUS_HOLDING_REGISTER | 760 | 1 |  | u8 | 0 | 1 | 1
id:4703 | MODBUS_HOLDING_REGISTER | 5272 | 1 |  | u8 | 0 | 1 | 0
id:4704 | MODBUS_HOLDING_REGISTER | 5273 | 1 |  | u8 | 0 | 1 | 0
id:4705 | MODBUS_HOLDING_REGISTER | 5274 | 1 |  | u8 | 0 | 1 | 0
id:4706 | MODBUS_HOLDING_REGISTER | 5275 | 1 |  | u8 | 0 | 1 | 0
id:4707 | MODBUS_HOLDING_REGISTER | 5276 | 1 |  | u8 | 0 | 1 | 0
id:4708 | MODBUS_HOLDING_REGISTER | 5277 | 1 |  | u8 | 0 | 1 | 0
id:4709 | MODBUS_HOLDING_REGISTER | 5278 | 1 |  | u8 | 0 | 1 | 0
id:4710 | MODBUS_HOLDING_REGISTER | 5279 | 1 |  | u8 | 0 | 1 | 0
Input AUX6 | MODBUS_HOLDING_REGISTER | 767 | 1 |  | u8 | 0 | 68 | 0
Operating mode circulation pump heating heat pump 1 | MODBUS_HOLDING_REGISTER | 783 | 1 |  | u8 | 0 | 1 | 1
Speed circulation pump waiting mode heat pump 1 | MODBUS_HOLDING_REGISTER | 841 | 1 | % | u8 | 1 | 100 | 30
Speed, circulation pump, standby mode (EB100) | MODBUS_HOLDING_REGISTER | 842 | 1 | % | u8 | 1 | 100 | 30
Activated (Smart Price Adaption) | MODBUS_HOLDING_REGISTER | 843 | 1 |  | u8 | 0 | 1 | 0
(SPA), cooling activated | MODBUS_HOLDING_REGISTER | 849 | 1 |  | u8 | 0 | 1 | 1
(SPA), area | MODBUS_HOLDING_REGISTER | 851 | 1 |  | u8 | 0 | 255 | 255
Internal shunt controlled additional heat | MODBUS_HOLDING_REGISTER | 857 | 1 |  | u8 | 0 | 1 | 0
Max. speed controlled charge pump (EB101) | MODBUS_HOLDING_REGISTER | 867 | 1 | % | u8 | 80 | 100 | 100
External adjustment climate system 8 | MODBUS_HOLDING_REGISTER | 893 | 1 |  | s8 | -10 | 10 | 0
External adjustment climate system 7 | MODBUS_HOLDING_REGISTER | 894 | 1 |  | s8 | -10 | 10 | 0
External adjustment climate system 6 | MODBUS_HOLDING_REGISTER | 895 | 1 |  | s8 | -10 | 10 | 0
External adjustment climate system 5 | MODBUS_HOLDING_REGISTER | 896 | 1 |  | s8 | -10 | 10 | 0
External adjustment with room sensor climate system 8 | MODBUS_HOLDING_REGISTER | 897 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor climate system 7 | MODBUS_HOLDING_REGISTER | 898 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor climate system 6 | MODBUS_HOLDING_REGISTER | 899 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor climate system 5 | MODBUS_HOLDING_REGISTER | 900 | 10 | °C | s16 | 50 | 300 | 200
Climate system 5 | MODBUS_HOLDING_REGISTER | 905 | 1 |  | u8 | 0 | 1 | 0
Climate system 6 | MODBUS_HOLDING_REGISTER | 906 | 1 |  | u8 | 0 | 1 | 0
Climate system 7 | MODBUS_HOLDING_REGISTER | 907 | 1 |  | u8 | 0 | 1 | 0
Climate system 8 | MODBUS_HOLDING_REGISTER | 908 | 1 |  | u8 | 0 | 1 | 0
Heating connected, climate system 1 | MODBUS_HOLDING_REGISTER | 932 | 1 |  | u8 | 0 | 1 | 1
ERS 1 | MODBUS_HOLDING_REGISTER | 933 | 1 |  | u8 | 0 | 1 | 0
EB103/104-GP12 | MODBUS_HOLDING_REGISTER | 939 | 1 |  | u8 | 0 | 1 | 0
EB105/106-GP12 | MODBUS_HOLDING_REGISTER | 940 | 1 |  | u8 | 0 | 1 | 0
EB107/108-GP12 | MODBUS_HOLDING_REGISTER | 941 | 1 |  | u8 | 0 | 1 | 0
blockFreq 2 (EB101) | MODBUS_HOLDING_REGISTER | 5295 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB101) | MODBUS_HOLDING_REGISTER | 5296 | 1 |  | u8 | 0 | 1 | 0
id:4971 | MODBUS_HOLDING_REGISTER | 5297 | 1 | Hz | u8 | 20 | 117 | 20
id:4972 | MODBUS_HOLDING_REGISTER | 5298 | 1 | Hz | u8 | 20 | 117 | 20
id:4973 | MODBUS_HOLDING_REGISTER | 5299 | 1 | Hz | u8 | 23 | 120 | 23
id:4974 | MODBUS_HOLDING_REGISTER | 5300 | 1 | Hz | u8 | 23 | 120 | 23
Use room sensor climate system 8 | MODBUS_HOLDING_REGISTER | 948 | 1 |  | u8 | 0 | 1 | 0
Use room sensor climate system 7 | MODBUS_HOLDING_REGISTER | 949 | 1 |  | u8 | 0 | 1 | 0
Use room sensor climate system 6 | MODBUS_HOLDING_REGISTER | 950 | 1 |  | u8 | 0 | 1 | 0
Use room sensor climate system 5 | MODBUS_HOLDING_REGISTER | 951 | 1 |  | u8 | 0 | 1 | 0
Room sensor set point value climate system 8 | MODBUS_HOLDING_REGISTER | 952 | 10 | °C | s16 | 50 | 300 | 200
Room sensor set point value climate system 7 | MODBUS_HOLDING_REGISTER | 953 | 10 | °C | s16 | 50 | 300 | 200
Room sensor set point value climate system 6 | MODBUS_HOLDING_REGISTER | 954 | 10 | °C | s16 | 50 | 300 | 200
Room sensor set point value climate system 5 | MODBUS_HOLDING_REGISTER | 955 | 10 | °C | s16 | 50 | 300 | 200
Room sensor factor climate system 8 | MODBUS_HOLDING_REGISTER | 956 | 10 |  | u8 | 0 | 60 | 20
Room sensor factor climate system 7 | MODBUS_HOLDING_REGISTER | 957 | 10 |  | u8 | 0 | 60 | 20
Room sensor factor climate system 6 | MODBUS_HOLDING_REGISTER | 958 | 10 |  | u8 | 0 | 60 | 20
Room sensor factor climate system 5 | MODBUS_HOLDING_REGISTER | 959 | 10 |  | u8 | 0 | 60 | 20
Current transformer ratio | MODBUS_HOLDING_REGISTER | 980 | 1 |  | u16 | 300 | 3000 | 300
Room sensor set point value climate system 8, cooling | MODBUS_HOLDING_REGISTER | 981 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 7, cooling | MODBUS_HOLDING_REGISTER | 982 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 6, cooling | MODBUS_HOLDING_REGISTER | 983 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 5, cooling | MODBUS_HOLDING_REGISTER | 984 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 4, cooling | MODBUS_HOLDING_REGISTER | 985 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 3, cooling | MODBUS_HOLDING_REGISTER | 986 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 2, cooling | MODBUS_HOLDING_REGISTER | 987 | 10 | °C | s16 | 50 | 350 | 250
Room sensor set point value climate system 1, cooling | MODBUS_HOLDING_REGISTER | 988 | 10 | °C | s16 | 50 | 350 | 250
Room sensor factor climate system 8, cooling | MODBUS_HOLDING_REGISTER | 989 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 7, cooling | MODBUS_HOLDING_REGISTER | 990 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 6, cooling | MODBUS_HOLDING_REGISTER | 991 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 5, cooling | MODBUS_HOLDING_REGISTER | 992 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 4, cooling | MODBUS_HOLDING_REGISTER | 993 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 3, cooling | MODBUS_HOLDING_REGISTER | 994 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 2, cooling | MODBUS_HOLDING_REGISTER | 995 | 10 |  | u8 | 0 | 60 | 10
Room sensor factor climate system 1, cooling | MODBUS_HOLDING_REGISTER | 996 | 10 |  | u8 | 0 | 60 | 10
Set point value (RH) | MODBUS_HOLDING_REGISTER | 997 | 1 | % | s8 | 30 | 90 | 60
HTS 1 | MODBUS_HOLDING_REGISTER | 998 | 1 |  | u8 | 0 | 1 | 0
OPT | MODBUS_HOLDING_REGISTER | 1015 | 1 |  | u8 | 0 | 1 | 0
DM start difference (OPT) | MODBUS_HOLDING_REGISTER | 1016 | 1 | DM | s16 | 10 | 2000 | 700
Exhaust air fan speed 4 (ERS 1) | MODBUS_HOLDING_REGISTER | 1021 | 1 | % | u8 | 0 | 100 | 100
Exhaust air fan speed 3 (ERS 1) | MODBUS_HOLDING_REGISTER | 1022 | 1 | % | u8 | 0 | 100 | 80
Exhaust air fan speed 2 (ERS 1) | MODBUS_HOLDING_REGISTER | 1023 | 1 | % | u8 | 0 | 100 | 30
Exhaust air fan speed 1 (ERS 1) | MODBUS_HOLDING_REGISTER | 1024 | 1 | % | u8 | 0 | 100 | 0
Exhaust air fan speed normal (ERS 1) | MODBUS_HOLDING_REGISTER | 1025 | 1 | % | u8 | 1 | 100 | 75
Filtering time (BT64) | MODBUS_HOLDING_REGISTER | 1027 | 1 | min | u8 | 5 | 30 | 5
(ACS) - Thermostat, hysteresis between compressors | MODBUS_HOLDING_REGISTER | 1028 | 1 | °C | s8 | 1 | 10 | 2
Start temperature (BT64) | MODBUS_HOLDING_REGISTER | 1029 | 1 | °C | s8 | -8 | 30 | 10
S135 | MODBUS_HOLDING_REGISTER | 1035 | 1 |  | u8 | 0 | 1 | 0
Pump speed (S135) | MODBUS_HOLDING_REGISTER | 1036 | 1 | % | u8 | 1 | 100 | 70
Bypass temp. (ERS 1) | MODBUS_HOLDING_REGISTER | 1044 | 1 | °C | u8 | 2 | 10 | 4
External cooling accessory pump type | MODBUS_HOLDING_REGISTER | 1046 | 1 |  | u8 | 0 | 1 | 1
Flow sensor activated X22 | MODBUS_HOLDING_REGISTER | 1049 | 1 |  | u8 | 0 | 1 | 0
Flow sensor activated X21 | MODBUS_HOLDING_REGISTER | 1050 | 1 |  | u8 | 0 | 1 | 0
Max. internal additional heat SG Ready | MODBUS_HOLDING_REGISTER | 1052 | 100 | kW | s16 | 0 | 900 | 700
Hysteresis (OPT) | MODBUS_HOLDING_REGISTER | 1066 | 1 |  | s16 | 10 | 2000 | 100
PV panel affects heating (EME) | MODBUS_HOLDING_REGISTER | 1069 | 1 |  | u8 | 0 | 1 | 0
PV panel affects hot water (EME) | MODBUS_HOLDING_REGISTER | 1070 | 1 |  | u8 | 0 | 1 | 0
Delay timer EME | MODBUS_HOLDING_REGISTER | 1071 | 1 |  | u16 | 0 | 0 | 0
Pump 4 (FLM) | MODBUS_HOLDING_REGISTER | 1074 | 1 |  | u8 | 0 | 1 | 0
Pump 3 (FLM) | MODBUS_HOLDING_REGISTER | 1075 | 1 |  | u8 | 0 | 1 | 0
Pump 2 (FLM) | MODBUS_HOLDING_REGISTER | 1076 | 1 |  | u8 | 0 | 1 | 0
Defrosting time (FLM 4) | MODBUS_HOLDING_REGISTER | 1077 | 1 | h | u8 | 1 | 30 | 10
Defrosting time (FLM 3) | MODBUS_HOLDING_REGISTER | 1078 | 1 | h | u8 | 1 | 30 | 10
Defrosting time (FLM 2) | MODBUS_HOLDING_REGISTER | 1079 | 1 | h | u8 | 1 | 30 | 10
Cooling (FLM 4) | MODBUS_HOLDING_REGISTER | 1080 | 1 |  | u8 | 0 | 1 | 0
Cooling (FLM 3) | MODBUS_HOLDING_REGISTER | 1081 | 1 |  | u8 | 0 | 1 | 0
Cooling (FLM 2) | MODBUS_HOLDING_REGISTER | 1082 | 1 |  | u8 | 0 | 1 | 0
Pump speed (FLM 4) | MODBUS_HOLDING_REGISTER | 1083 | 1 | % | u8 | 1 | 100 | 100
Pump speed (FLM 3) | MODBUS_HOLDING_REGISTER | 1084 | 1 | % | u8 | 1 | 100 | 100
Pump speed (FLM 2) | MODBUS_HOLDING_REGISTER | 1085 | 1 | % | u8 | 1 | 100 | 100
Pump speed (FLM 1) | MODBUS_HOLDING_REGISTER | 1086 | 1 | % | u8 | 1 | 100 | 100
AUX blocking (OPT) | MODBUS_HOLDING_REGISTER | 1095 | 1 |  | u8 | 0 | 0 | 0
Outdoor air mixing | MODBUS_HOLDING_REGISTER | 1096 | 1 |  | u8 | 0 | 1 | 0
Smart home room control | MODBUS_HOLDING_REGISTER | 1102 | 1 |  | u8 | 0 | 1 | 0
Smart Energy Source | MODBUS_HOLDING_REGISTER | 1105 | 1 |  | u8 | 0 | 1 | 0
Control method, smart energy source | MODBUS_HOLDING_REGISTER | 1106 | 1 |  | u8 | 0 | 1 | 0
El. price, special, smart energy source | MODBUS_HOLDING_REGISTER | 1107 | 1 |  | u8 | 0 | 2 | 0
El. price, fixed, smart energy source | MODBUS_HOLDING_REGISTER | 1108 | 1 |  | u16 | 0 | 10000 | 100
El. price, smart energy source | MODBUS_HOLDING_REGISTER | 1109 | 1 |  | u8 | 0 | 1 | 0
El. price, fixed, smart energy source | MODBUS_HOLDING_REGISTER | 1110 | 1 |  | u16 | 0 | 10000 | 100
El. price, smart energy source | MODBUS_HOLDING_REGISTER | 1111 | 1 |  | u8 | 0 | 3 | 0
El. price, fixed, smart energy source | MODBUS_HOLDING_REGISTER | 1112 | 1 |  | u16 | 0 | 10000 | 100
El. price, smart energy source | MODBUS_HOLDING_REGISTER | 1113 | 1 |  | u8 | 0 | 1 | 0
El. price, fixed, smart energy source | MODBUS_HOLDING_REGISTER | 1114 | 1 |  | u16 | 0 | 10000 | 100
El. price, smart energy source | MODBUS_HOLDING_REGISTER | 1115 | 1 |  | u8 | 0 | 1 | 0
El. price, fixed, smart energy source | MODBUS_HOLDING_REGISTER | 1116 | 1 |  | u16 | 0 | 10000 | 100
Prim. factor, smart energy source | MODBUS_HOLDING_REGISTER | 1117 | 10 |  | u8 | 0 | 50 | 25
Prim. factor, shunt add. heat smart energy source | MODBUS_HOLDING_REGISTER | 1118 | 10 |  | u8 | 0 | 50 | 10
Prim. factor, ext. step add. heat smart energy source | MODBUS_HOLDING_REGISTER | 1119 | 10 |  | u8 | 0 | 50 | 10
Prim. factor, OPT10 smart energy source | MODBUS_HOLDING_REGISTER | 1120 | 10 |  | u8 | 0 | 50 | 10
OPT10, high tariff price smart energy source | MODBUS_HOLDING_REGISTER | 1121 | 1 |  | u16 | 1 | 10000 | 100
OPT10, low tariff price smart energy source | MODBUS_HOLDING_REGISTER | 1122 | 1 |  | u16 | 1 | 10000 | 100
ext. step add. heat, high tariff price smart energy source | MODBUS_HOLDING_REGISTER | 1123 | 1 |  | u16 | 1 | 10000 | 100
ext. step add. heat, low tariff price smart energy source | MODBUS_HOLDING_REGISTER | 1124 | 1 |  | u16 | 1 | 10000 | 100
Shunt add. heat, high tariff price smart energy source | MODBUS_HOLDING_REGISTER | 1125 | 1 |  | u16 | 1 | 10000 | 100
Shunt add. heat, low tariff price smart energy source | MODBUS_HOLDING_REGISTER | 1126 | 1 |  | u16 | 1 | 10000 | 100
El. price, fixed, high tariff smart energy source | MODBUS_HOLDING_REGISTER | 1127 | 1 |  | u16 | 1 | 10000 | 100
El. price, fixed, low tariff smart energy source | MODBUS_HOLDING_REGISTER | 1128 | 1 |  | u16 | 1 | 10000 | 100
El. price, variable, high tariff smart energy source | MODBUS_HOLDING_REGISTER | 1129 | 1 |  | u16 | 1 | 10000 | 100
El. price, variable, low tariff smart energy source | MODBUS_HOLDING_REGISTER | 1130 | 1 |  | u16 | 1 | 10000 | 100
DM start source, priority 5 smart energy source | MODBUS_HOLDING_REGISTER | 1131 | 1 |  | s16 | 100 | 2000 | 400
DM start source, priority 4 smart energy source | MODBUS_HOLDING_REGISTER | 1132 | 1 |  | s16 | 100 | 2000 | 400
DM start source, priority 3 smart energy source | MODBUS_HOLDING_REGISTER | 1133 | 1 |  | s16 | 100 | 2000 | 400
DM start source, priority 2 smart energy source | MODBUS_HOLDING_REGISTER | 1134 | 1 |  | s16 | 100 | 2000 | 400
DM start source, priority 1 smart energy source | MODBUS_HOLDING_REGISTER | 1135 | 1 |  | s16 | -2000 | -10 | -60
Start day, tariff smart energy source | MODBUS_HOLDING_REGISTER | 1136 | 1 |  | u8 | 1 | 31 | 1
End day, tariff smart energy source | MODBUS_HOLDING_REGISTER | 1137 | 1 |  | u8 | 1 | 31 | 31
Start month, tariff smart energy source | MODBUS_HOLDING_REGISTER | 1138 | 1 |  | u8 | 1 | 12 | 1
End month, tariff smart energy source | MODBUS_HOLDING_REGISTER | 1139 | 1 |  | u8 | 1 | 12 | 12
Start day, fixed tariff smart energy source | MODBUS_HOLDING_REGISTER | 1172 | 1 |  | u8 | 1 | 31 | 1
End day, fixed tariff smart energy source | MODBUS_HOLDING_REGISTER | 1173 | 1 |  | u8 | 1 | 31 | 31
Start month, fixed tariff smart energy source | MODBUS_HOLDING_REGISTER | 1174 | 1 |  | u8 | 1 | 12 | 1
End month, fixed tariff smart energy source | MODBUS_HOLDING_REGISTER | 1175 | 1 |  | u8 | 1 | 12 | 12
Start day, tariff OPT10 smart energy source | MODBUS_HOLDING_REGISTER | 1208 | 1 |  | u8 | 1 | 31 | 1
End day, tariff OPT10 smart energy source | MODBUS_HOLDING_REGISTER | 1209 | 1 |  | u8 | 1 | 31 | 31
Start month, tariff OPT10 smart energy source | MODBUS_HOLDING_REGISTER | 1210 | 1 |  | u8 | 1 | 12 | 1
End month, tariff OPT10 smart energy source | MODBUS_HOLDING_REGISTER | 1211 | 1 |  | u8 | 1 | 12 | 12
Start day tariff, shunt additional heat smart energy source | MODBUS_HOLDING_REGISTER | 1244 | 1 |  | u8 | 1 | 31 | 1
End day tariff, shunt additional heat smart energy source | MODBUS_HOLDING_REGISTER | 1245 | 1 |  | u8 | 1 | 31 | 31
Start month tariff, shunt additional heat smart energy source | MODBUS_HOLDING_REGISTER | 1246 | 1 |  | u8 | 1 | 12 | 1
End month tariff, shunt additional heat smart energy source | MODBUS_HOLDING_REGISTER | 1247 | 1 |  | u8 | 1 | 12 | 12
Start day tariff, ext. step add. heat smart energy source | MODBUS_HOLDING_REGISTER | 1280 | 1 |  | u8 | 1 | 31 | 1
End day tariff, ext. step add. heat smart energy source | MODBUS_HOLDING_REGISTER | 1281 | 1 |  | u8 | 1 | 31 | 31
Start month tariff, ext. step add. heat smart energy source | MODBUS_HOLDING_REGISTER | 1282 | 1 |  | u8 | 1 | 12 | 1
End month tariff, ext. step add. heat smart energy source | MODBUS_HOLDING_REGISTER | 1283 | 1 |  | u8 | 1 | 12 | 12
Ground water pump temperature alarm | MODBUS_HOLDING_REGISTER | 1316 | 1 |  | u8 | 0 | 1 | 0
Ground water pump temperature alarm level | MODBUS_HOLDING_REGISTER | 1317 | 1 | °C | s8 | -15 | 20 | 3
Brine pump auto mode | MODBUS_HOLDING_REGISTER | 1319 | 1 |  | s8 | 0 | 2 | 1
Max difference, SES priority 1 energy source | MODBUS_HOLDING_REGISTER | 1326 | 10 | °C | s16 | 10 | 250 | 100
Max difference, SES lower priority energy source | MODBUS_HOLDING_REGISTER | 1327 | 10 | °C | s16 | 10 | 250 | 70
Installed (EB101) | MODBUS_HOLDING_REGISTER | 1550 | 1 |  | u8 | 0 | 1 | 1
EME20 | MODBUS_HOLDING_REGISTER | 4000 | 1 |  | u8 | 0 | 1 | 0
Current power | MODBUS_INPUT_REGISTER | 2176 | 1 | W | u32 | 0 | 0 | 0
Ground water pump's control signal | MODBUS_HOLDING_REGISTER | 4012 | 1 |  | s8 | 0 | 0 | 0
id:6028 | MODBUS_INPUT_REGISTER | 1993 | 1 |  | u8 | 0 | 0 | 0
id:6029 | MODBUS_INPUT_REGISTER | 1994 | 1 |  | u16 | 0 | 0 | 0
Total average power (Solar PV) | MODBUS_INPUT_REGISTER | 2178 | 100 | kW | u32 | 0 | 0 | 0
Total energy | MODBUS_INPUT_REGISTER | 2180 | 10 | kWh | s32 | 0 | 0 | 0
ERS 2 | MODBUS_HOLDING_REGISTER | 4076 | 1 |  | u8 | 0 | 1 | 0
ERS 3 | MODBUS_HOLDING_REGISTER | 4077 | 1 |  | u8 | 0 | 1 | 0
ERS 4 | MODBUS_HOLDING_REGISTER | 4078 | 1 |  | u8 | 0 | 1 | 0
id:6486 | MODBUS_HOLDING_REGISTER | 4135 | 1 |  | u8 | 0 | 1 | 0
id:6756 | MODBUS_INPUT_REGISTER | 2004 | 10 | %RH | s16 | 0 | 0 | 0
id:6757 | MODBUS_INPUT_REGISTER | 2005 | 10 | %RH | s16 | 0 | 0 | 0
id:6758 | MODBUS_INPUT_REGISTER | 2006 | 10 | %RH | s16 | 0 | 0 | 0
HTS 2 | MODBUS_HOLDING_REGISTER | 1981 | 1 |  | u8 | 0 | 1 | 0
HTS 3 | MODBUS_HOLDING_REGISTER | 1982 | 1 |  | u8 | 0 | 1 | 0
HTS 4 | MODBUS_HOLDING_REGISTER | 1983 | 1 |  | u8 | 0 | 1 | 0
External adjustment, cooling climate system 8 | MODBUS_HOLDING_REGISTER | 4138 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 7 | MODBUS_HOLDING_REGISTER | 4139 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 6 | MODBUS_HOLDING_REGISTER | 4140 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 5 | MODBUS_HOLDING_REGISTER | 4141 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 4 | MODBUS_HOLDING_REGISTER | 4142 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 3 | MODBUS_HOLDING_REGISTER | 4143 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 2 | MODBUS_HOLDING_REGISTER | 4144 | 1 |  | s8 | -10 | 10 | 0
External adjustment, cooling climate system 1 | MODBUS_HOLDING_REGISTER | 4145 | 1 |  | s8 | -10 | 10 | 0
External adjustment with room sensor, cooling climate system 8 | MODBUS_HOLDING_REGISTER | 4146 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 7 | MODBUS_HOLDING_REGISTER | 4147 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 6 | MODBUS_HOLDING_REGISTER | 4148 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 5 | MODBUS_HOLDING_REGISTER | 4149 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 4 | MODBUS_HOLDING_REGISTER | 4150 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 3 | MODBUS_HOLDING_REGISTER | 4151 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 2 | MODBUS_HOLDING_REGISTER | 4152 | 10 | °C | s16 | 50 | 300 | 200
External adjustment with room sensor, cooling climate system 1 | MODBUS_HOLDING_REGISTER | 4153 | 10 | °C | s16 | 50 | 300 | 200
id:6917 | MODBUS_HOLDING_REGISTER | 4072 | 1 |  | s16 | 0 | 200 | 1
id:6918 | MODBUS_HOLDING_REGISTER | 4073 | 1 |  | s16 | 0 | 20 | 1
id:6920 | MODBUS_HOLDING_REGISTER | 4074 | 1 |  | s16 | 0 | 20 | 0
id:6921 | MODBUS_HOLDING_REGISTER | 4075 | 1 |  | s16 | 1 | 100 | 15
id:6922 | MODBUS_HOLDING_REGISTER | 4154 | 10 |  | s16 | 0 | 200 | 30
id:6923 | MODBUS_HOLDING_REGISTER | 4155 | 1 |  | s16 | 0 | 20 | 2
blockFreq 1 (EB102) | MODBUS_HOLDING_REGISTER | 4164 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB103) | MODBUS_HOLDING_REGISTER | 4165 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB104) | MODBUS_HOLDING_REGISTER | 4166 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB105) | MODBUS_HOLDING_REGISTER | 4167 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB106) | MODBUS_HOLDING_REGISTER | 4168 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB107) | MODBUS_HOLDING_REGISTER | 4169 | 1 |  | u8 | 0 | 1 | 0
blockFreq 1 (EB108) | MODBUS_HOLDING_REGISTER | 4170 | 1 |  | u8 | 0 | 1 | 0
id:6977 | MODBUS_HOLDING_REGISTER | 4201 | 1 |  | u8 | 0 | 100 | 0
Power at DOT, manual value | MODBUS_HOLDING_REGISTER | 4200 | 1 |  | u8 | 0 | 1 | 0
Blocking actions (ERS 3) | MODBUS_HOLDING_REGISTER | 4100 | 1 |  | u8 | 0 | 2 | 2
Blocking actions (ERS 4) | MODBUS_HOLDING_REGISTER | 4101 | 1 |  | u8 | 0 | 2 | 2
id:7048 | MODBUS_HOLDING_REGISTER | 5227 | 1 |  | u8 | 0 | 1 | 0
id:7122 | MODBUS_INPUT_REGISTER | 2401 | 10 | V | s8 | 0 | 0 | 0
id:7123 | MODBUS_INPUT_REGISTER | 2402 | 10 | V | s8 | 0 | 0 | 0
id:7124 | MODBUS_INPUT_REGISTER | 2403 | 10 | V | s8 | 0 | 0 | 0
id:7125 | MODBUS_INPUT_REGISTER | 2404 | 10 | V | s8 | 0 | 0 | 0
id:7126 | MODBUS_INPUT_REGISTER | 2405 | 10 | V | s8 | 0 | 0 | 0
id:7127 | MODBUS_INPUT_REGISTER | 2406 | 10 | V | s8 | 0 | 0 | 0
id:7128 | MODBUS_INPUT_REGISTER | 2407 | 10 | V | s8 | 0 | 0 | 0
id:7138 | MODBUS_HOLDING_REGISTER | 5441 | 1 | % | u8 | 0 | 100 | 70
id:7139 | MODBUS_HOLDING_REGISTER | 5442 | 1 |  | u8 | 0 | 1 | 0
id:7140 | MODBUS_HOLDING_REGISTER | 5443 | 1 |  | u8 | 0 | 1 | 0
id:7141 | MODBUS_HOLDING_REGISTER | 5444 | 1 | % | u8 | 0 | 100 | 70
id:7142 | MODBUS_HOLDING_REGISTER | 5445 | 1 |  | u8 | 0 | 1 | 0
id:7143 | MODBUS_HOLDING_REGISTER | 5446 | 1 |  | u8 | 0 | 1 | 0
id:7144 | MODBUS_HOLDING_REGISTER | 5447 | 1 | % | u8 | 0 | 100 | 70
id:7145 | MODBUS_HOLDING_REGISTER | 5448 | 1 |  | u8 | 0 | 1 | 0
id:7146 | MODBUS_HOLDING_REGISTER | 5449 | 1 |  | u8 | 0 | 1 | 0
id:7147 | MODBUS_HOLDING_REGISTER | 5450 | 1 | % | u8 | 0 | 100 | 70
id:7148 | MODBUS_HOLDING_REGISTER | 5451 | 1 |  | u8 | 0 | 1 | 0
id:7149 | MODBUS_HOLDING_REGISTER | 5452 | 1 |  | u8 | 0 | 1 | 0
id:7150 | MODBUS_HOLDING_REGISTER | 5453 | 1 | % | u8 | 0 | 100 | 70
id:7176 | MODBUS_HOLDING_REGISTER | 5455 | 1 |  | u8 | 0 | 1 | 0
id:7943 | MODBUS_INPUT_REGISTER | 2399 | 10 | % | u16 | 0 | 0 | 0
id:7944 | MODBUS_INPUT_REGISTER | 2400 | 10 | % | u16 | 0 | 0 | 0
id:8002 | MODBUS_HOLDING_REGISTER | 1996 | 1 | % | s8 | -15 | 10 | -3
id:8003 | MODBUS_HOLDING_REGISTER | 1997 | 1 | % | u8 | 1 | 254 | 65
Minimum permitted speed (EB101 GP12) | MODBUS_HOLDING_REGISTER | 5352 | 1 | % | u8 | 1 | 50 | 1
Start fan de-icing (EB101) | MODBUS_HOLDING_REGISTER | 5360 | 1 |  | s8 | 0 | 1 | 0
Defrost Requested EB101 | MODBUS_HOLDING_REGISTER | 5368 | 1 |  | s8 | 0 | 1 | 0
System 1 (RMU) | MODBUS_HOLDING_REGISTER | 176 | 1 |  | u8 | 0 | 1 | 0
System 2 (RMU) | MODBUS_HOLDING_REGISTER | 177 | 1 |  | u8 | 0 | 1 | 0
System 3 (RMU) | MODBUS_HOLDING_REGISTER | 178 | 1 |  | u8 | 0 | 1 | 0
System 4 (RMU) | MODBUS_HOLDING_REGISTER | 179 | 1 |  | u8 | 0 | 1 | 0
System 4 (RMU) | MODBUS_HOLDING_REGISTER | 1998 | 1 |  | u8 | 0 | 1 | 0
System 4 (RMU) | MODBUS_HOLDING_REGISTER | 1999 | 1 |  | u8 | 0 | 1 | 0
System 4 (RMU) | MODBUS_HOLDING_REGISTER | 2000 | 1 |  | u8 | 0 | 1 | 0
System 4 (RMU) | MODBUS_HOLDING_REGISTER | 2001 | 1 |  | u8 | 0 | 1 | 0
id:8302 | MODBUS_HOLDING_REGISTER | 5388 | 1 |  | u8 | 0 | 0 | 0
id:8982 | MODBUS_HOLDING_REGISTER | 5390 | 1 |  | u8 | 0 | 0 | 0
The start guide has been run | MODBUS_HOLDING_REGISTER | 2742 | 1 |  | u8 | 0 | 1 | 1
Audio signal on alarm | MODBUS_HOLDING_REGISTER | 5326 | 1 |  | u8 | 0 | 1 | 1
Sound when pressing button | MODBUS_HOLDING_REGISTER | 5327 | 1 |  | u8 | 0 | 1 | 1
BT12 offset, heat pump 1 | MODBUS_HOLDING_REGISTER | 5328 | 10 | °C | s8 | -50 | 50 | 0
Additional heat step, emergency mode | MODBUS_HOLDING_REGISTER | 3058 | 1 |  | u8 | 0 | 7 | 0
Heating, auto | MODBUS_HOLDING_REGISTER | 3059 | 1 |  | u8 | 0 | 1 | 1
Factor | MODBUS_HOLDING_REGISTER | 3033 | 1 |  | u8 | 1 | 10 | 5
id:10881 | MODBUS_HOLDING_REGISTER | 3062 | 1 |  | u8 | 0 | 1 | 0
id:10890 | MODBUS_HOLDING_REGISTER | 3063 | 1 |  | u8 | 0 | 1 | 0
id:12332 | MODBUS_HOLDING_REGISTER | 2767 | 1 |  | s16 | -32768 | 32767 | -32768
id:12333 | MODBUS_HOLDING_REGISTER | 2768 | 1 |  | s16 | -32768 | 32767 | -32768
id:12334 | MODBUS_HOLDING_REGISTER | 2769 | 1 |  | s16 | -32768 | 32767 | -32768
id:12335 | MODBUS_HOLDING_REGISTER | 2770 | 1 |  | s16 | -32768 | 32767 | -32768
id:12336 | MODBUS_HOLDING_REGISTER | 2771 | 1 |  | s16 | -32768 | 32767 | -32768
id:12337 | MODBUS_HOLDING_REGISTER | 2772 | 1 |  | s16 | -32768 | 32767 | -32768
id:12338 | MODBUS_HOLDING_REGISTER | 2773 | 1 |  | s16 | -32768 | 32767 | -32768
id:12339 | MODBUS_HOLDING_REGISTER | 2774 | 1 |  | s16 | -32768 | 32767 | -32768
id:12340 | MODBUS_HOLDING_REGISTER | 2775 | 1 |  | s16 | -32768 | 32767 | -32768
id:12341 | MODBUS_HOLDING_REGISTER | 2776 | 1 |  | s16 | -32768 | 32767 | -32768
id:12342 | MODBUS_HOLDING_REGISTER | 2777 | 1 |  | s16 | -32768 | 32767 | -32768
id:12343 | MODBUS_HOLDING_REGISTER | 2778 | 1 |  | s16 | -32768 | 32767 | -32768
id:12344 | MODBUS_HOLDING_REGISTER | 2779 | 1 |  | s16 | -32768 | 32767 | -32768
id:12345 | MODBUS_HOLDING_REGISTER | 2780 | 1 |  | s16 | -32768 | 32767 | -32768
id:12346 | MODBUS_HOLDING_REGISTER | 2781 | 1 |  | s16 | -32768 | 32767 | -32768
id:12347 | MODBUS_HOLDING_REGISTER | 2782 | 1 |  | s16 | -32768 | 32767 | -32768
id:12348 | MODBUS_HOLDING_REGISTER | 2783 | 1 |  | s16 | -32768 | 32767 | -32768
id:12349 | MODBUS_HOLDING_REGISTER | 2784 | 1 |  | s16 | -32768 | 32767 | -32768
id:12350 | MODBUS_HOLDING_REGISTER | 2785 | 1 |  | s16 | -32768 | 32767 | -32768
id:12351 | MODBUS_HOLDING_REGISTER | 2786 | 1 |  | s16 | -32768 | 32767 | -32768
id:12352 | MODBUS_HOLDING_REGISTER | 2787 | 1 |  | s16 | -32768 | 32767 | -32768
id:12353 | MODBUS_HOLDING_REGISTER | 2788 | 1 |  | s16 | -32768 | 32767 | -32768
id:12354 | MODBUS_HOLDING_REGISTER | 2789 | 1 |  | s16 | -32768 | 32767 | -32768
id:12355 | MODBUS_HOLDING_REGISTER | 2790 | 1 |  | s16 | -32768 | 32767 | -32768
id:12356 | MODBUS_HOLDING_REGISTER | 2791 | 1 |  | s16 | -32768 | 32767 | -32768
id:12357 | MODBUS_HOLDING_REGISTER | 2792 | 1 |  | s16 | -32768 | 32767 | -32768
id:12358 | MODBUS_HOLDING_REGISTER | 2793 | 1 |  | s16 | -32768 | 32767 | -32768
id:12359 | MODBUS_HOLDING_REGISTER | 2794 | 1 |  | s16 | -32768 | 32767 | -32768
id:12360 | MODBUS_HOLDING_REGISTER | 2795 | 1 |  | s16 | -32768 | 32767 | -32768
id:12361 | MODBUS_HOLDING_REGISTER | 2796 | 1 |  | s16 | -32768 | 32767 | -32768
id:12362 | MODBUS_HOLDING_REGISTER | 2797 | 1 |  | s16 | -32768 | 32767 | -32768
id:12363 | MODBUS_HOLDING_REGISTER | 2798 | 1 |  | s16 | -32768 | 32767 | -32768
id:12364 | MODBUS_HOLDING_REGISTER | 2799 | 1 |  | s16 | -32768 | 32767 | -32768
id:12365 | MODBUS_HOLDING_REGISTER | 2800 | 1 |  | s16 | -32768 | 32767 | -32768
id:12366 | MODBUS_HOLDING_REGISTER | 2801 | 1 |  | s16 | -32768 | 32767 | -32768
id:12367 | MODBUS_HOLDING_REGISTER | 2802 | 1 |  | s16 | -32768 | 32767 | -32768
id:12368 | MODBUS_HOLDING_REGISTER | 2803 | 1 |  | s16 | -32768 | 32767 | -32768
id:12369 | MODBUS_HOLDING_REGISTER | 2804 | 1 |  | s16 | -32768 | 32767 | -32768
id:12370 | MODBUS_HOLDING_REGISTER | 2805 | 1 |  | s16 | -32768 | 32767 | -32768
id:12371 | MODBUS_HOLDING_REGISTER | 2806 | 1 |  | s16 | -32768 | 32767 | -32768
id:12372 | MODBUS_HOLDING_REGISTER | 2807 | 1 |  | s16 | -32768 | 32767 | -32768
id:12373 | MODBUS_HOLDING_REGISTER | 2808 | 1 |  | s16 | -32768 | 32767 | -32768
id:12374 | MODBUS_HOLDING_REGISTER | 2809 | 1 |  | s16 | -32768 | 32767 | -32768
id:12375 | MODBUS_HOLDING_REGISTER | 2810 | 1 |  | s16 | -32768 | 32767 | -32768
id:12376 | MODBUS_HOLDING_REGISTER | 2811 | 1 |  | s16 | -32768 | 32767 | -32768
id:12377 | MODBUS_HOLDING_REGISTER | 2812 | 1 |  | s16 | -32768 | 32767 | -32768
id:12378 | MODBUS_HOLDING_REGISTER | 2813 | 1 |  | s16 | -32768 | 32767 | -32768
id:12379 | MODBUS_HOLDING_REGISTER | 2814 | 1 |  | s16 | -32768 | 32767 | -32768
id:12380 | MODBUS_HOLDING_REGISTER | 2815 | 1 |  | s16 | -32768 | 32767 | -32768
id:12381 | MODBUS_HOLDING_REGISTER | 2816 | 1 |  | s16 | -32768 | 32767 | -32768
id:12382 | MODBUS_HOLDING_REGISTER | 2817 | 1 |  | s16 | -32768 | 32767 | -32768
id:12383 | MODBUS_HOLDING_REGISTER | 2818 | 1 |  | s16 | -32768 | 32767 | -32768
id:12384 | MODBUS_HOLDING_REGISTER | 2819 | 1 |  | s16 | -32768 | 32767 | -32768
Period | MODBUS_HOLDING_REGISTER | 3088 | 1 |  | u8 | 0 | 1 | 0
Number of years | MODBUS_HOLDING_REGISTER | 3089 | 1 |  | u8 | 1 | 10 | 1
Months | MODBUS_HOLDING_REGISTER | 3090 | 1 |  | u32 | 0 | 4095 | 4095
Show outdoor temperature | MODBUS_HOLDING_REGISTER | 3096 | 1 |  | u8 | 0 | 0 | 0
Show indoor temperature | MODBUS_HOLDING_REGISTER | 3097 | 1 |  | u8 | 0 | 0 | 0
Active days | MODBUS_HOLDING_REGISTER | 3066 | 1 |  | u8 | 0 | 127 | 0
Active days | MODBUS_HOLDING_REGISTER | 3067 | 1 |  | u8 | 0 | 127 | 0
Active days | MODBUS_HOLDING_REGISTER | 3068 | 1 |  | u8 | 0 | 127 | 0
Active days | MODBUS_HOLDING_REGISTER | 3069 | 1 |  | u8 | 0 | 127 | 0
Active days | MODBUS_HOLDING_REGISTER | 3070 | 1 |  | u8 | 0 | 127 | 0
Start time | MODBUS_HOLDING_REGISTER | 5393 | 1 |  | -
Start time | MODBUS_HOLDING_REGISTER | 5397 | 1 |  | -
Stop time | MODBUS_HOLDING_REGISTER | 5401 | 1 |  | -
AUX relay (AUX11) | MODBUS_HOLDING_REGISTER | 224 | 1 |  | u8 | 0 | 30 | 5
id:12650 | MODBUS_HOLDING_REGISTER | 3104 | 1 |  | -
id:12651 | MODBUS_HOLDING_REGISTER | 3144 | 1 |  | -
id:12652 | MODBUS_HOLDING_REGISTER | 3184 | 1 |  | -
id:12653 | MODBUS_HOLDING_REGISTER | 3224 | 1 |  | -
id:12654 | MODBUS_HOLDING_REGISTER | 3264 | 1 |  | -
id:12655 | MODBUS_HOLDING_REGISTER | 3304 | 1 |  | -
id:12656 | MODBUS_HOLDING_REGISTER | 3344 | 1 |  | -
id:12657 | MODBUS_HOLDING_REGISTER | 3384 | 1 |  | -
id:12658 | MODBUS_HOLDING_REGISTER | 3424 | 1 |  | -
id:12659 | MODBUS_HOLDING_REGISTER | 3464 | 1 |  | -
id:12660 | MODBUS_HOLDING_REGISTER | 3504 | 1 |  | -
id:12661 | MODBUS_HOLDING_REGISTER | 3544 | 1 |  | -
id:12662 | MODBUS_HOLDING_REGISTER | 3584 | 1 |  | -
id:12663 | MODBUS_HOLDING_REGISTER | 3624 | 1 |  | -
id:12664 | MODBUS_HOLDING_REGISTER | 3664 | 1 |  | -
id:12665 | MODBUS_HOLDING_REGISTER | 3704 | 1 |  | -
id:12666 | MODBUS_HOLDING_REGISTER | 3744 | 1 |  | -
id:12667 | MODBUS_HOLDING_REGISTER | 3784 | 1 |  | -
id:12668 | MODBUS_HOLDING_REGISTER | 3824 | 1 |  | -
id:12669 | MODBUS_HOLDING_REGISTER | 3864 | 1 |  | -
id:12670 | MODBUS_HOLDING_REGISTER | 3904 | 1 |  | -
id:12671 | MODBUS_HOLDING_REGISTER | 2978 | 1 |  | u8 | 0 | 3 | 0
id:12672 | MODBUS_HOLDING_REGISTER | 2979 | 1 |  | u8 | 0 | 3 | 0
id:12673 | MODBUS_HOLDING_REGISTER | 2980 | 1 |  | u8 | 0 | 3 | 0
id:12674 | MODBUS_HOLDING_REGISTER | 2981 | 1 |  | u8 | 0 | 3 | 0
id:12675 | MODBUS_HOLDING_REGISTER | 2982 | 1 |  | u8 | 0 | 3 | 0
id:12676 | MODBUS_HOLDING_REGISTER | 2983 | 1 |  | u8 | 0 | 3 | 0
id:12677 | MODBUS_HOLDING_REGISTER | 2984 | 1 |  | u8 | 0 | 3 | 0
id:12678 | MODBUS_HOLDING_REGISTER | 2985 | 1 |  | u8 | 0 | 3 | 0
id:12679 | MODBUS_HOLDING_REGISTER | 2986 | 1 |  | u8 | 0 | 15 | 0
id:12680 | MODBUS_HOLDING_REGISTER | 2987 | 1 |  | u8 | 0 | 15 | 0
id:12681 | MODBUS_HOLDING_REGISTER | 2988 | 1 |  | u8 | 0 | 15 | 0
id:12682 | MODBUS_HOLDING_REGISTER | 2989 | 1 |  | u8 | 0 | 15 | 0
id:12683 | MODBUS_HOLDING_REGISTER | 2990 | 1 |  | u8 | 0 | 15 | 0
id:12684 | MODBUS_HOLDING_REGISTER | 2991 | 1 |  | u8 | 0 | 15 | 0
id:12685 | MODBUS_HOLDING_REGISTER | 2992 | 1 |  | u8 | 0 | 15 | 0
id:12686 | MODBUS_HOLDING_REGISTER | 2993 | 1 |  | u8 | 0 | 15 | 0
id:12687 | MODBUS_HOLDING_REGISTER | 2994 | 1 |  | u8 | 0 | 15 | 0
id:12688 | MODBUS_HOLDING_REGISTER | 2995 | 1 |  | u8 | 0 | 15 | 0
id:12689 | MODBUS_HOLDING_REGISTER | 2996 | 1 |  | u8 | 0 | 15 | 0
id:12690 | MODBUS_HOLDING_REGISTER | 2997 | 1 |  | u8 | 0 | 15 | 0
id:12691 | MODBUS_HOLDING_REGISTER | 2998 | 1 |  | u8 | 0 | 3 | 0
id:12692 | MODBUS_HOLDING_REGISTER | 3944 | 1 |  | u32 | 0 | 0 | 0
id:12693 | MODBUS_HOLDING_REGISTER | 3946 | 1 |  | u32 | 0 | 0 | 0
id:12694 | MODBUS_HOLDING_REGISTER | 3948 | 1 |  | u32 | 0 | 0 | 0
id:12695 | MODBUS_HOLDING_REGISTER | 3950 | 1 |  | u32 | 0 | 0 | 0
id:12696 | MODBUS_HOLDING_REGISTER | 3952 | 1 |  | u32 | 0 | 0 | 0
id:12697 | MODBUS_HOLDING_REGISTER | 3954 | 1 |  | u32 | 0 | 0 | 0
id:12698 | MODBUS_HOLDING_REGISTER | 3956 | 1 |  | u32 | 0 | 0 | 0
id:12699 | MODBUS_HOLDING_REGISTER | 3958 | 1 |  | u32 | 0 | 0 | 0
id:12700 | MODBUS_HOLDING_REGISTER | 3960 | 1 |  | u32 | 0 | 0 | 0
id:12701 | MODBUS_HOLDING_REGISTER | 3962 | 1 |  | u32 | 0 | 0 | 0
id:12702 | MODBUS_HOLDING_REGISTER | 3964 | 1 |  | u32 | 0 | 0 | 0
id:12703 | MODBUS_HOLDING_REGISTER | 3966 | 1 |  | u32 | 0 | 0 | 0
id:12704 | MODBUS_HOLDING_REGISTER | 3968 | 1 |  | u32 | 0 | 0 | 0
id:12705 | MODBUS_HOLDING_REGISTER | 3970 | 1 |  | u32 | 0 | 0 | 0
id:12706 | MODBUS_HOLDING_REGISTER | 3972 | 1 |  | u32 | 0 | 0 | 0
id:12707 | MODBUS_HOLDING_REGISTER | 3974 | 1 |  | u32 | 0 | 0 | 0
id:12708 | MODBUS_HOLDING_REGISTER | 3976 | 1 |  | u32 | 0 | 0 | 0
id:12709 | MODBUS_HOLDING_REGISTER | 3978 | 1 |  | u32 | 0 | 0 | 0
id:12710 | MODBUS_HOLDING_REGISTER | 3980 | 1 |  | u32 | 0 | 0 | 0
id:12711 | MODBUS_HOLDING_REGISTER | 3982 | 1 |  | u32 | 0 | 0 | 0
id:12712 | MODBUS_HOLDING_REGISTER | 3984 | 1 |  | u32 | 0 | 0 | 0
id:12801 | MODBUS_HOLDING_REGISTER | 2505 | 10 | °C | s32 | 50 | 350 | 200
id:12802 | MODBUS_HOLDING_REGISTER | 2507 | 10 | °C | s32 | 50 | 350 | 200
id:12803 | MODBUS_HOLDING_REGISTER | 2509 | 10 | °C | s32 | 50 | 350 | 200
id:12804 | MODBUS_HOLDING_REGISTER | 2511 | 10 | °C | s32 | 50 | 350 | 200
id:12805 | MODBUS_HOLDING_REGISTER | 2513 | 10 | °C | s32 | 50 | 350 | 200
id:12806 | MODBUS_HOLDING_REGISTER | 2515 | 10 | °C | s32 | 50 | 350 | 200
id:12807 | MODBUS_HOLDING_REGISTER | 2517 | 10 | °C | s32 | 50 | 350 | 200
id:12808 | MODBUS_HOLDING_REGISTER | 2519 | 10 | °C | s32 | 50 | 350 | 200
id:12809 | MODBUS_HOLDING_REGISTER | 2521 | 10 | °C | s32 | 50 | 350 | 200
id:12810 | MODBUS_HOLDING_REGISTER | 2523 | 10 | °C | s32 | 50 | 350 | 200
id:12811 | MODBUS_HOLDING_REGISTER | 2525 | 10 | °C | s32 | 50 | 350 | 200
id:12812 | MODBUS_HOLDING_REGISTER | 2527 | 10 | °C | s32 | 50 | 350 | 200
id:12813 | MODBUS_HOLDING_REGISTER | 2529 | 10 | °C | s32 | 50 | 350 | 200
id:12814 | MODBUS_HOLDING_REGISTER | 2531 | 10 | °C | s32 | 50 | 350 | 200
id:12815 | MODBUS_HOLDING_REGISTER | 2533 | 10 | °C | s32 | 50 | 350 | 200
id:12816 | MODBUS_HOLDING_REGISTER | 2535 | 10 | °C | s32 | 50 | 350 | 200
id:12817 | MODBUS_HOLDING_REGISTER | 2537 | 10 | °C | s32 | 50 | 350 | 200
id:12818 | MODBUS_HOLDING_REGISTER | 2539 | 10 | °C | s32 | 50 | 350 | 200
id:12819 | MODBUS_HOLDING_REGISTER | 2541 | 10 | °C | s32 | 50 | 350 | 200
id:12820 | MODBUS_HOLDING_REGISTER | 2543 | 10 | °C | s32 | 50 | 350 | 200
id:12821 | MODBUS_HOLDING_REGISTER | 2545 | 10 | °C | s32 | 50 | 350 | 200
id:12822 | MODBUS_HOLDING_REGISTER | 2547 | 10 | °C | s32 | 50 | 350 | 200
id:12823 | MODBUS_HOLDING_REGISTER | 2549 | 10 | °C | s32 | 50 | 350 | 200
id:12824 | MODBUS_HOLDING_REGISTER | 2551 | 10 | °C | s32 | 50 | 350 | 200
id:12825 | MODBUS_HOLDING_REGISTER | 2553 | 10 | °C | s32 | 50 | 350 | 200
id:12826 | MODBUS_HOLDING_REGISTER | 2555 | 10 | °C | s32 | 50 | 350 | 200
id:12827 | MODBUS_HOLDING_REGISTER | 2557 | 10 | °C | s32 | 50 | 350 | 200
id:12828 | MODBUS_HOLDING_REGISTER | 2559 | 10 | °C | s32 | 50 | 350 | 200
id:12829 | MODBUS_HOLDING_REGISTER | 2561 | 10 | °C | s32 | 50 | 350 | 200
id:12830 | MODBUS_HOLDING_REGISTER | 2563 | 10 | °C | s32 | 50 | 350 | 200
id:12831 | MODBUS_HOLDING_REGISTER | 2565 | 10 | °C | s32 | 50 | 350 | 200
id:12832 | MODBUS_HOLDING_REGISTER | 2567 | 10 | °C | s32 | 50 | 350 | 200
id:12833 | MODBUS_HOLDING_REGISTER | 2569 | 10 | °C | s32 | 50 | 350 | 200
id:12834 | MODBUS_HOLDING_REGISTER | 2571 | 10 | °C | s32 | 50 | 350 | 200
id:12835 | MODBUS_HOLDING_REGISTER | 2573 | 10 | °C | s32 | 50 | 350 | 200
id:12836 | MODBUS_HOLDING_REGISTER | 2575 | 10 | °C | s32 | 50 | 350 | 200
id:12837 | MODBUS_HOLDING_REGISTER | 2577 | 10 | °C | s32 | 50 | 350 | 200
id:12838 | MODBUS_HOLDING_REGISTER | 2579 | 10 | °C | s32 | 50 | 350 | 200
id:12839 | MODBUS_HOLDING_REGISTER | 2581 | 10 | °C | s32 | 50 | 350 | 200
id:12840 | MODBUS_HOLDING_REGISTER | 2583 | 10 | °C | s32 | 50 | 350 | 200
id:12841 | MODBUS_HOLDING_REGISTER | 2585 | 10 | °C | s32 | 50 | 350 | 250
id:12842 | MODBUS_HOLDING_REGISTER | 2587 | 10 | °C | s32 | 50 | 350 | 250
id:12843 | MODBUS_HOLDING_REGISTER | 2589 | 10 | °C | s32 | 50 | 350 | 250
id:12844 | MODBUS_HOLDING_REGISTER | 2591 | 10 | °C | s32 | 50 | 350 | 250
id:12845 | MODBUS_HOLDING_REGISTER | 2593 | 10 | °C | s32 | 50 | 350 | 250
id:12846 | MODBUS_HOLDING_REGISTER | 2595 | 10 | °C | s32 | 50 | 350 | 250
id:12847 | MODBUS_HOLDING_REGISTER | 2597 | 10 | °C | s32 | 50 | 350 | 250
id:12848 | MODBUS_HOLDING_REGISTER | 2599 | 10 | °C | s32 | 50 | 350 | 250
id:12849 | MODBUS_HOLDING_REGISTER | 2601 | 10 | °C | s32 | 50 | 350 | 250
id:12850 | MODBUS_HOLDING_REGISTER | 2603 | 10 | °C | s32 | 50 | 350 | 250
id:12851 | MODBUS_HOLDING_REGISTER | 2605 | 10 | °C | s32 | 50 | 350 | 250
id:12852 | MODBUS_HOLDING_REGISTER | 2607 | 10 | °C | s32 | 50 | 350 | 250
id:12853 | MODBUS_HOLDING_REGISTER | 2609 | 10 | °C | s32 | 50 | 350 | 250
id:12854 | MODBUS_HOLDING_REGISTER | 2611 | 10 | °C | s32 | 50 | 350 | 250
id:12855 | MODBUS_HOLDING_REGISTER | 2613 | 10 | °C | s32 | 50 | 350 | 250
id:12856 | MODBUS_HOLDING_REGISTER | 2615 | 10 | °C | s32 | 50 | 350 | 250
id:12857 | MODBUS_HOLDING_REGISTER | 2617 | 10 | °C | s32 | 50 | 350 | 250
id:12858 | MODBUS_HOLDING_REGISTER | 2619 | 10 | °C | s32 | 50 | 350 | 250
id:12859 | MODBUS_HOLDING_REGISTER | 2621 | 10 | °C | s32 | 50 | 350 | 250
id:12860 | MODBUS_HOLDING_REGISTER | 2623 | 10 | °C | s32 | 50 | 350 | 250
id:12861 | MODBUS_HOLDING_REGISTER | 2625 | 10 | °C | s32 | 50 | 350 | 250
id:12862 | MODBUS_HOLDING_REGISTER | 2627 | 10 | °C | s32 | 50 | 350 | 250
id:12863 | MODBUS_HOLDING_REGISTER | 2629 | 10 | °C | s32 | 50 | 350 | 250
id:12864 | MODBUS_HOLDING_REGISTER | 2631 | 10 | °C | s32 | 50 | 350 | 250
id:12865 | MODBUS_HOLDING_REGISTER | 2633 | 10 | °C | s32 | 50 | 350 | 250
id:12866 | MODBUS_HOLDING_REGISTER | 2635 | 10 | °C | s32 | 50 | 350 | 250
id:12867 | MODBUS_HOLDING_REGISTER | 2637 | 10 | °C | s32 | 50 | 350 | 250
id:12868 | MODBUS_HOLDING_REGISTER | 2639 | 10 | °C | s32 | 50 | 350 | 250
id:12869 | MODBUS_HOLDING_REGISTER | 2641 | 10 | °C | s32 | 50 | 350 | 250
id:12870 | MODBUS_HOLDING_REGISTER | 2643 | 10 | °C | s32 | 50 | 350 | 250
id:12871 | MODBUS_HOLDING_REGISTER | 2645 | 10 | °C | s32 | 50 | 350 | 250
id:12872 | MODBUS_HOLDING_REGISTER | 2647 | 10 | °C | s32 | 50 | 350 | 250
id:12873 | MODBUS_HOLDING_REGISTER | 2649 | 10 | °C | s32 | 50 | 350 | 250
id:12874 | MODBUS_HOLDING_REGISTER | 2651 | 10 | °C | s32 | 50 | 350 | 250
id:12875 | MODBUS_HOLDING_REGISTER | 2653 | 10 | °C | s32 | 50 | 350 | 250
id:12876 | MODBUS_HOLDING_REGISTER | 2655 | 10 | °C | s32 | 50 | 350 | 250
id:12877 | MODBUS_HOLDING_REGISTER | 2657 | 10 | °C | s32 | 50 | 350 | 250
id:12878 | MODBUS_HOLDING_REGISTER | 2659 | 10 | °C | s32 | 50 | 350 | 250
id:12879 | MODBUS_HOLDING_REGISTER | 2661 | 10 | °C | s32 | 50 | 350 | 250
id:12880 | MODBUS_HOLDING_REGISTER | 2663 | 10 | °C | s32 | 50 | 350 | 250
id:13655 | MODBUS_INPUT_REGISTER | 2411 | 1 |  | u8 | 0 | 0 | 0
id:13656 | MODBUS_INPUT_REGISTER | 2412 | 1 |  | u8 | 0 | 0 | 0
id:13796 | MODBUS_INPUT_REGISTER | 2243 | 1 |  | u8 | 0 | 0 | 0
id:13797 | MODBUS_INPUT_REGISTER | 2244 | 1 |  | u8 | 0 | 0 | 0
id:13798 | MODBUS_INPUT_REGISTER | 2245 | 1 |  | u8 | 0 | 0 | 0
id:13799 | MODBUS_INPUT_REGISTER | 2246 | 1 |  | u8 | 0 | 0 | 0
id:13800 | MODBUS_INPUT_REGISTER | 2247 | 1 |  | u8 | 0 | 0 | 0
id:13801 | MODBUS_INPUT_REGISTER | 2248 | 1 |  | u8 | 0 | 0 | 0
id:13802 | MODBUS_INPUT_REGISTER | 2249 | 1 |  | u8 | 0 | 0 | 0
id:13803 | MODBUS_INPUT_REGISTER | 2250 | 1 |  | u8 | 0 | 0 | 0
Offset cooling (Solar PV) | MODBUS_HOLDING_REGISTER | 2667 | 1 |  | s8 | -10 | 0 | -1
Offset heating (Solar PV) | MODBUS_HOLDING_REGISTER | 2668 | 1 |  | u8 | 0 | 10 | 1
Offset pool (Solar PV) | MODBUS_HOLDING_REGISTER | 2669 | 1 | °C | u8 | 0 | 10 | 10
Cooling (Solar PV) | MODBUS_HOLDING_REGISTER | 2666 | 1 |  | u8 | 0 | 1 | 0
AUX (Solar PV) | MODBUS_HOLDING_REGISTER | 2675 | 1 |  | u8 | 0 | 1 | 0
id:14052 | MODBUS_HOLDING_REGISTER | 2670 | 1 | kW | u32 | 1 | 999 | 1
id:14061 | MODBUS_HOLDING_REGISTER | 2672 | 1 |  | u8 | 0 | 1 | 0
Temperature, Overload, pool | MODBUS_HOLDING_REGISTER | 0 | 1 | °C | u8 | 1 | 50 | 1
Modbus TCP/IP Ext. (Solar PV) | MODBUS_HOLDING_REGISTER | 2107 | 1 |  | u8 | 0 | 1 | 0
Modbus TCP/IP Ext.Include own consumption (Solar PV) | MODBUS_HOLDING_REGISTER | 2108 | 1 |  | u8 | 0 | 1 | 0
Modbus TCP/IP Ext. Available power (Solar PV) | MODBUS_HOLDING_REGISTER | 2109 | 1 |  | u16 | 0 | 65535 | 0
External adjustment input, main unit (ECS1) | MODBUS_HOLDING_REGISTER | 2111 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS2) | MODBUS_HOLDING_REGISTER | 2112 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS3) | MODBUS_HOLDING_REGISTER | 2113 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS4) | MODBUS_HOLDING_REGISTER | 2114 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS5) | MODBUS_HOLDING_REGISTER | 2115 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS6) | MODBUS_HOLDING_REGISTER | 2116 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS7) | MODBUS_HOLDING_REGISTER | 2117 | 1 |  | u8 | 0 | 1 | 0
External adjustment input (ECS8) | MODBUS_HOLDING_REGISTER | 2118 | 1 |  | u8 | 0 | 1 | 0
Zone 1 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2119 | 1 |  | u8 | 0 | 1 | 0
Zone 2 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2120 | 1 |  | u8 | 0 | 1 | 0
Zone 3 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2121 | 1 |  | u8 | 0 | 1 | 0
Zone 4 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2122 | 1 |  | u8 | 0 | 1 | 0
Zone 5 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2123 | 1 |  | u8 | 0 | 1 | 0
Zone 6 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2124 | 1 |  | u8 | 0 | 1 | 0
Zone 7 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2125 | 1 |  | u8 | 0 | 1 | 0
Zone 8 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2126 | 1 |  | u8 | 0 | 1 | 0
Zone 9 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2127 | 1 |  | u8 | 0 | 1 | 0
Zone 10 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2128 | 1 |  | u8 | 0 | 1 | 0
Zone 11 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2129 | 1 |  | u8 | 0 | 1 | 0
Zone 12 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2130 | 1 |  | u8 | 0 | 1 | 0
Zone 13 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2131 | 1 |  | u8 | 0 | 1 | 0
Zone 14 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2132 | 1 |  | u8 | 0 | 1 | 0
Zone 15 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2133 | 1 |  | u8 | 0 | 1 | 0
Zone 16 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2134 | 1 |  | u8 | 0 | 1 | 0
Zone 17 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2135 | 1 |  | u8 | 0 | 1 | 0
Zone 18 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2136 | 1 |  | u8 | 0 | 1 | 0
Zone 19 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2137 | 1 |  | u8 | 0 | 1 | 0
Zone 20 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2138 | 1 |  | u8 | 0 | 1 | 0
Zone 21 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2139 | 1 |  | u8 | 0 | 1 | 0
Zone 22 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2140 | 1 |  | u8 | 0 | 1 | 0
Zone 23 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2141 | 1 |  | u8 | 0 | 1 | 0
Zone 24 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2142 | 1 |  | u8 | 0 | 1 | 0
Zone 25 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2143 | 1 |  | u8 | 0 | 1 | 0
Zone 26 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2144 | 1 |  | u8 | 0 | 1 | 0
Zone 27 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2145 | 1 |  | u8 | 0 | 1 | 0
Zone 28 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2146 | 1 |  | u8 | 0 | 1 | 0
Zone 29 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2147 | 1 |  | u8 | 0 | 1 | 0
Zone 30 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2148 | 1 |  | u8 | 0 | 1 | 0
Zone 31 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2149 | 1 |  | u8 | 0 | 1 | 0
Zone 32 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2150 | 1 |  | u8 | 0 | 1 | 0
Zone 33 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2151 | 1 |  | u8 | 0 | 1 | 0
Zone 34 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2152 | 1 |  | u8 | 0 | 1 | 0
Zone 35 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2153 | 1 |  | u8 | 0 | 1 | 0
Zone 36 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2154 | 1 |  | u8 | 0 | 1 | 0
Zone 37 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2155 | 1 |  | u8 | 0 | 1 | 0
Zone 38 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2156 | 1 |  | u8 | 0 | 1 | 0
Zone 39 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2157 | 1 |  | u8 | 0 | 1 | 0
Zone 40 affected by ECS1 | MODBUS_HOLDING_REGISTER | 2158 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS1 | MODBUS_HOLDING_REGISTER | 2439 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS2 | MODBUS_HOLDING_REGISTER | 2440 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS3 | MODBUS_HOLDING_REGISTER | 2441 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS4 | MODBUS_HOLDING_REGISTER | 2442 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS5 | MODBUS_HOLDING_REGISTER | 2443 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS6 | MODBUS_HOLDING_REGISTER | 2444 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS7 | MODBUS_HOLDING_REGISTER | 2445 | 1 |  | u8 | 0 | 1 | 0
Input on ECS1 affects ECS8 | MODBUS_HOLDING_REGISTER | 2446 | 1 |  | u8 | 0 | 1 | 0
External setting for adjustment migrated | MODBUS_HOLDING_REGISTER | 2503 | 1 |  | u8 | 0 | 1 | 0
Max. step internal additional heat | MODBUS_HOLDING_REGISTER | 2504 | 1 |  | u8 | 0 | 7 | 3
Version, inverter (EB101) | MODBUS_INPUT_REGISTER | 2147 | 1 |  | u8 | 0 | 0 | 0
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2676 | 1 |  | u8 | 1 | 24 | 3
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2677 | 1 |  | u8 | 1 | 24 | 3
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2678 | 1 |  | u8 | 1 | 24 | 3
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2679 | 1 |  | u8 | 1 | 24 | 3
Total oper. time ext. add. heat, heating | MODBUS_INPUT_REGISTER | 2182 | 10 | h | s32 | 0 | 9999999 | 0
Total HW run time additional heat | MODBUS_INPUT_REGISTER | 2184 | 10 | h | s32 | 0 | 9999999 | 0
id:21077 | MODBUS_HOLDING_REGISTER | 3020 | 1 |  | u8 | 0 | 0 | 0
id:21078 | MODBUS_HOLDING_REGISTER | 3021 | 1 |  | u8 | 0 | 0 | 0
id:21079 | MODBUS_HOLDING_REGISTER | 3022 | 1 |  | u8 | 0 | 0 | 0
id:21080 | MODBUS_HOLDING_REGISTER | 3023 | 1 |  | u8 | 0 | 0 | 0
id:21081 | MODBUS_HOLDING_REGISTER | 3024 | 1 |  | u8 | 0 | 0 | 0
id:21082 | MODBUS_HOLDING_REGISTER | 3025 | 1 |  | u8 | 0 | 0 | 0
id:21083 | MODBUS_HOLDING_REGISTER | 3026 | 1 |  | u8 | 0 | 0 | 0
id:21084 | MODBUS_HOLDING_REGISTER | 3027 | 1 |  | u8 | 0 | 0 | 0
id:21189 | MODBUS_INPUT_REGISTER | 2726 | 1 |  | u16 | 0 | 0 | 0
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2700 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2701 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2702 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2703 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2704 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2705 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2706 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2707 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2708 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2709 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2710 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2711 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2712 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2713 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2714 | 1 | h | u8 | 1 | 24 | 4
Return time fan 4 | MODBUS_HOLDING_REGISTER | 2715 | 1 | h | u8 | 1 | 24 | 4
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2728 | 1 |  | u8 | 1 | 24 | 3
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2729 | 1 |  | u8 | 1 | 24 | 3
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2730 | 1 |  | u8 | 1 | 24 | 3
Time between filter replacement | MODBUS_HOLDING_REGISTER | 2731 | 1 |  | u8 | 1 | 24 | 3
AUX from Modbus | MODBUS_HOLDING_REGISTER | 2740 | 1 |  | u8 | 0 | 68 | 0
AUX from Modbus | MODBUS_HOLDING_REGISTER | 2741 | 1 |  | s16 | 0 | 0 | 0
Heat pump test - Silent mode (EB101/EB102) | MODBUS_HOLDING_REGISTER | 5101 | 1 |  | u8 | 0 | 1 | 0
Last defrost, heat pump 1 | MODBUS_INPUT_REGISTER | 2158 | 1 |  | u8 | 0 | 255 | 255
ERS 2 | MODBUS_HOLDING_REGISTER | 2820 | 1 |  | u8 | 0 | 1 | 0
ERS 3 | MODBUS_HOLDING_REGISTER | 2821 | 1 |  | u8 | 0 | 1 | 0
ERS 4 | MODBUS_HOLDING_REGISTER | 2822 | 1 |  | u8 | 0 | 1 | 0
ERS 4 | MODBUS_HOLDING_REGISTER | 2823 | 1 |  | u8 | 0 | 1 | 0
ERS 4 | MODBUS_HOLDING_REGISTER | 2824 | 1 |  | u8 | 0 | 1 | 1
ERS 4 | MODBUS_HOLDING_REGISTER | 2825 | 1 |  | u8 | 0 | 1 | 1
ERS 4 | MODBUS_HOLDING_REGISTER | 2826 | 1 |  | u8 | 0 | 1 | 1
ERS 4 | MODBUS_HOLDING_REGISTER | 2827 | 1 |  | u8 | 0 | 1 | 1
Min. vent temp. (ERS 4) | MODBUS_HOLDING_REGISTER | 2857 | 1 | °C | u8 | 0 | 10 | 3
Min. vent temp. (ERS 4) | MODBUS_HOLDING_REGISTER | 2858 | 1 | °C | u8 | 0 | 10 | 3
Min. vent temp. (ERS 4) | MODBUS_HOLDING_REGISTER | 2859 | 1 | °C | u8 | 0 | 10 | 3
Min. vent temp. (ERS 4) | MODBUS_HOLDING_REGISTER | 2860 | 1 | °C | u8 | 0 | 10 | 3
Blocking actions (ERS 4) | MODBUS_HOLDING_REGISTER | 2828 | 1 |  | u8 | 0 | 2 | 2
Blocking actions (ERS 4) | MODBUS_HOLDING_REGISTER | 2829 | 1 |  | u8 | 0 | 2 | 2
Blocking actions (ERS 4) | MODBUS_HOLDING_REGISTER | 2830 | 1 |  | u8 | 0 | 2 | 2
Blocking actions (ERS 4) | MODBUS_HOLDING_REGISTER | 2831 | 1 |  | u8 | 0 | 2 | 2
id:23145 | MODBUS_HOLDING_REGISTER | 2921 | 1 |  | u8 | 0 | 1 | 0
id:23146 | MODBUS_HOLDING_REGISTER | 2922 | 1 |  | u8 | 0 | 1 | 0
id:23147 | MODBUS_HOLDING_REGISTER | 2923 | 1 |  | u8 | 0 | 1 | 0
id:23148 | MODBUS_HOLDING_REGISTER | 2924 | 1 |  | u8 | 0 | 1 | 0
id:23149 | MODBUS_HOLDING_REGISTER | 2836 | 10 | °C | s16 | -200 | 410 | 190
id:23150 | MODBUS_HOLDING_REGISTER | 2837 | 10 | °C | s16 | -200 | 410 | 190
id:23151 | MODBUS_HOLDING_REGISTER | 2838 | 10 | °C | s16 | -200 | 410 | 190
id:23152 | MODBUS_HOLDING_REGISTER | 2839 | 10 | °C | s16 | -200 | 410 | 190
id:23153 | MODBUS_HOLDING_REGISTER | 2832 | 10 | °C | s16 | 30 | 100 | 30
id:23154 | MODBUS_HOLDING_REGISTER | 2833 | 10 | °C | s16 | 30 | 100 | 30
id:23155 | MODBUS_HOLDING_REGISTER | 2834 | 10 | °C | s16 | 30 | 100 | 30
id:23156 | MODBUS_HOLDING_REGISTER | 2835 | 10 | °C | s16 | 30 | 100 | 30
Fan mode 5 | MODBUS_INPUT_REGISTER | 2168 | 1 | % | u8 | 0 | 0 | 0
Fan mode 6 | MODBUS_INPUT_REGISTER | 2169 | 1 | % | u8 | 0 | 0 | 0
Fan mode 7 | MODBUS_INPUT_REGISTER | 2170 | 1 | % | u8 | 0 | 0 | 0
Fan mode 8 | MODBUS_INPUT_REGISTER | 2171 | 1 | % | u8 | 0 | 0 | 0
Disable emergency restart GP1 | MODBUS_HOLDING_REGISTER | 5392 | 1 |  | u8 | 0 | 1 | 0
Disable emergency restart GP1 | MODBUS_HOLDING_REGISTER | 5025 | 1 |  | u8 | 0 | 1 | 0
Modbus external control | MODBUS_HOLDING_REGISTER | 5008 | 1 |  | u8 | 0 | 1 | 0
id:24484 | MODBUS_HOLDING_REGISTER | 5009 | 10 | °C | s16 | 50 | 800 | 450
id:24485 | MODBUS_HOLDING_REGISTER | 5010 | 10 | °C | s16 | 50 | 800 | 450
id:24486 | MODBUS_HOLDING_REGISTER | 5011 | 10 | °C | s16 | 50 | 800 | 450
id:24487 | MODBUS_HOLDING_REGISTER | 5012 | 10 | °C | s16 | 50 | 800 | 450
id:24488 | MODBUS_HOLDING_REGISTER | 5013 | 10 | °C | s16 | 50 | 800 | 450
id:24489 | MODBUS_HOLDING_REGISTER | 5014 | 10 | °C | s16 | 50 | 800 | 450
id:24490 | MODBUS_HOLDING_REGISTER | 5015 | 10 | °C | s16 | 50 | 800 | 450
id:24491 | MODBUS_HOLDING_REGISTER | 5016 | 10 | °C | s16 | 50 | 800 | 450
id:24492 | MODBUS_HOLDING_REGISTER | 5017 | 10 | °C | s16 | -50 | 300 | 250
id:24493 | MODBUS_HOLDING_REGISTER | 5018 | 10 | °C | s16 | -50 | 300 | 250
id:24494 | MODBUS_HOLDING_REGISTER | 5019 | 10 | °C | s16 | -50 | 300 | 250
id:24495 | MODBUS_HOLDING_REGISTER | 5020 | 10 | °C | s16 | -50 | 300 | 250
id:24496 | MODBUS_HOLDING_REGISTER | 5021 | 10 | °C | s16 | -50 | 300 | 250
id:24497 | MODBUS_HOLDING_REGISTER | 5022 | 10 | °C | s16 | -50 | 300 | 250
id:24498 | MODBUS_HOLDING_REGISTER | 5023 | 10 | °C | s16 | -50 | 300 | 250
id:24499 | MODBUS_HOLDING_REGISTER | 5024 | 10 | °C | s16 | -50 | 300 | 250
id:24681 | MODBUS_HOLDING_REGISTER | 5056 | 1 |  | u8 | 0 | 1 | 0
id:24682 | MODBUS_HOLDING_REGISTER | 5057 | 1 |  | u8 | 0 | 1 | 0
id:24683 | MODBUS_HOLDING_REGISTER | 5058 | 1 |  | u8 | 0 | 255 | 0
id:24684 | MODBUS_HOLDING_REGISTER | 5059 | 1 |  | u8 | 0 | 1 | 0
Relay status | MODBUS_INPUT_REGISTER | 0 | 1 |  | u8 | 0 | 0 | 0
id:24969 | MODBUS_HOLDING_REGISTER | 5060 | 1 |  | u8 | 0 | 1 | 0
id:24970 | MODBUS_HOLDING_REGISTER | 5061 | 1 |  | s16 | -100 | 10000 | 0
id:24971 | MODBUS_HOLDING_REGISTER | 5062 | 1 |  | u8 | 0 | 1 | 0
id:24972 | MODBUS_HOLDING_REGISTER | 5063 | 1 |  | u16 | 0 | 1000 | 0
id:24973 | MODBUS_HOLDING_REGISTER | 5064 | 1 |  | u8 | 0 | 1 | 0
id:24974 | MODBUS_HOLDING_REGISTER | 5065 | 1 |  | u8 | 0 | 1 | 0
id:24975 | MODBUS_HOLDING_REGISTER | 5066 | 1 |  | u16 | 0 | 1000 | 0
id:24976 | MODBUS_HOLDING_REGISTER | 5067 | 1 |  | u8 | 0 | 1 | 0
id:24977 | MODBUS_HOLDING_REGISTER | 5068 | 1 |  | u8 | 0 | 1 | 0
id:24978 | MODBUS_HOLDING_REGISTER | 5069 | 1 |  | u16 | 0 | 1000 | 0
id:24979 | MODBUS_HOLDING_REGISTER | 5070 | 1 |  | u8 | 0 | 1 | 0
id:24980 | MODBUS_HOLDING_REGISTER | 5071 | 1 |  | u16 | 0 | 1000 | 0
Energy log - Produced energy for heating over the past hour | MODBUS_INPUT_REGISTER | 2283 | 100 | kWh | u32 | 0 | 0 | 0
Energy log - Used energy for heating over the past hour | MODBUS_INPUT_REGISTER | 2291 | 100 | kWh | u32 | 0 | 0 | 0
Energy log - Used energy by additional heater for heating over the past hour | MODBUS_INPUT_REGISTER | 2299 | 100 | kWh | u32 | 0 | 0 | 0
Energy log - Current power consumption | MODBUS_INPUT_REGISTER | 2305 | 100 | kWh | u32 | 0 | 0 | 0
Energy log - Current power consumption, components | MODBUS_INPUT_REGISTER | 2408 | 100 | kWh | u32 | 0 | 0 | 0
Compressor, total time energy storage, main unit (EP14) | MODBUS_INPUT_REGISTER | 2335 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, main unit (EP15) | MODBUS_INPUT_REGISTER | 2337 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 1 (EP14) | MODBUS_INPUT_REGISTER | 2339 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 1 (EP15) | MODBUS_INPUT_REGISTER | 2341 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 2 (EP14) | MODBUS_INPUT_REGISTER | 2343 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 2 (EP15) | MODBUS_INPUT_REGISTER | 2345 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 3 (EP14) | MODBUS_INPUT_REGISTER | 2347 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 3 (EP15) | MODBUS_INPUT_REGISTER | 2349 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 4 (EP14) | MODBUS_INPUT_REGISTER | 2351 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 4 (EP15) | MODBUS_INPUT_REGISTER | 2353 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 5 (EP14) | MODBUS_INPUT_REGISTER | 2355 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 5 (EP15) | MODBUS_INPUT_REGISTER | 2357 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 6 (EP14) | MODBUS_INPUT_REGISTER | 2359 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 6 (EP15) | MODBUS_INPUT_REGISTER | 2361 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 7 (EP14) | MODBUS_INPUT_REGISTER | 2363 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 7 (EP15) | MODBUS_INPUT_REGISTER | 2365 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 8 (EP14) | MODBUS_INPUT_REGISTER | 2367 | 1 | h | u32 | 0 | 2147483647 | 0
Compressor, total time energy storage, heat pump 8 (EP15) | MODBUS_INPUT_REGISTER | 2369 | 1 | h | u32 | 0 | 2147483647 | 0
id:26694 | MODBUS_HOLDING_REGISTER | 5208 | 1 |  | u8 | 0 | 1 | 0
id:26695 | MODBUS_HOLDING_REGISTER | 5209 | 1 |  | u8 | 0 | 1 | 0
id:26696 | MODBUS_HOLDING_REGISTER | 5210 | 1 |  | u8 | 0 | 1 | 0
id:26697 | MODBUS_HOLDING_REGISTER | 5211 | 1 |  | u8 | 0 | 1 | 0
id:26698 | MODBUS_HOLDING_REGISTER | 5212 | 1 |  | u8 | 0 | 1 | 0
id:26699 | MODBUS_HOLDING_REGISTER | 5213 | 1 |  | u8 | 0 | 1 | 0
id:26702 | MODBUS_HOLDING_REGISTER | 5216 | 1 |  | u8 | 0 | 1 | 0
id:26703 | MODBUS_HOLDING_REGISTER | 5217 | 10 | °C | s16 | 0 | 0 | 0
id:26704 | MODBUS_HOLDING_REGISTER | 5218 | 10 | °C | s16 | 0 | 0 | 0
id:26705 | MODBUS_HOLDING_REGISTER | 5219 | 10 | °C | s16 | 0 | 0 | 0
id:26706 | MODBUS_HOLDING_REGISTER | 5220 | 10 | °C | s16 | 0 | 0 | 0
id:26707 | MODBUS_HOLDING_REGISTER | 5221 | 10 | °C | s16 | 0 | 0 | 0
id:26708 | MODBUS_HOLDING_REGISTER | 5222 | 10 | °C | s16 | 0 | 0 | 0
id:26711 | MODBUS_HOLDING_REGISTER | 5225 | 10 | °C | s16 | 0 | 0 | 0
id:26793 | MODBUS_INPUT_REGISTER | 2375 | 1 |  | u8 | 0 | 7 | 7
id:26794 | MODBUS_INPUT_REGISTER | 2376 | 1 |  | u8 | 0 | 7 | 7
id:26795 | MODBUS_INPUT_REGISTER | 2377 | 1 |  | u8 | 0 | 7 | 7
id:26796 | MODBUS_INPUT_REGISTER | 2378 | 1 |  | u8 | 0 | 7 | 7
id:26797 | MODBUS_INPUT_REGISTER | 2379 | 1 |  | u8 | 0 | 7 | 7
id:26798 | MODBUS_INPUT_REGISTER | 2380 | 1 |  | u8 | 0 | 7 | 7
id:26799 | MODBUS_INPUT_REGISTER | 2381 | 1 |  | u8 | 0 | 7 | 7
id:26800 | MODBUS_INPUT_REGISTER | 2382 | 1 |  | u8 | 0 | 7 | 7
id:26801 | MODBUS_INPUT_REGISTER | 2383 | 1 |  | u8 | 0 | 7 | 7
id:26802 | MODBUS_INPUT_REGISTER | 2384 | 1 |  | u8 | 0 | 7 | 7
id:26803 | MODBUS_INPUT_REGISTER | 2385 | 1 |  | u8 | 0 | 7 | 7
id:26804 | MODBUS_INPUT_REGISTER | 2386 | 1 |  | u8 | 0 | 7 | 7
id:26805 | MODBUS_INPUT_REGISTER | 2387 | 1 |  | u8 | 0 | 7 | 7
id:26806 | MODBUS_INPUT_REGISTER | 2388 | 1 |  | u8 | 0 | 7 | 7
id:26807 | MODBUS_INPUT_REGISTER | 2389 | 1 |  | u8 | 0 | 7 | 7
id:26808 | MODBUS_INPUT_REGISTER | 2390 | 1 |  | u8 | 0 | 7 | 7
id:26809 | MODBUS_INPUT_REGISTER | 2391 | 1 |  | u8 | 0 | 7 | 7
id:26810 | MODBUS_INPUT_REGISTER | 2392 | 1 |  | u8 | 0 | 7 | 7
id:26811 | MODBUS_INPUT_REGISTER | 2393 | 1 |  | u8 | 0 | 7 | 7
id:26812 | MODBUS_INPUT_REGISTER | 2394 | 1 |  | u8 | 0 | 7 | 7
id:26813 | MODBUS_INPUT_REGISTER | 2395 | 1 |  | u8 | 0 | 7 | 7
id:26814 | MODBUS_INPUT_REGISTER | 2396 | 1 |  | u8 | 0 | 7 | 7
id:26815 | MODBUS_INPUT_REGISTER | 2397 | 1 |  | u8 | 0 | 7 | 7
id:26816 | MODBUS_INPUT_REGISTER | 2398 | 1 |  | u8 | 0 | 7 | 7
id:26817 | MODBUS_HOLDING_REGISTER | 5183 | 1 |  | s16 | -32768 | 32767 | 32767
id:26818 | MODBUS_HOLDING_REGISTER | 5184 | 1 |  | s16 | -32768 | 32767 | 32767
id:26819 | MODBUS_HOLDING_REGISTER | 5185 | 1 |  | s16 | -32768 | 32767 | 32767
id:26820 | MODBUS_HOLDING_REGISTER | 5186 | 1 |  | s16 | -32768 | 32767 | 32767
id:26821 | MODBUS_HOLDING_REGISTER | 5187 | 1 |  | s16 | -32768 | 32767 | 32767
id:26822 | MODBUS_HOLDING_REGISTER | 5188 | 1 |  | s16 | -32768 | 32767 | 32767
id:26823 | MODBUS_HOLDING_REGISTER | 5189 | 1 |  | s16 | -32768 | 32767 | 32767
id:26824 | MODBUS_HOLDING_REGISTER | 5190 | 1 |  | s16 | -32768 | 32767 | 32767
id:26825 | MODBUS_HOLDING_REGISTER | 5191 | 1 |  | s16 | -32768 | 32767 | 32767
id:26826 | MODBUS_HOLDING_REGISTER | 5192 | 1 |  | s16 | -32768 | 32767 | 32767
id:26827 | MODBUS_HOLDING_REGISTER | 5193 | 1 |  | s16 | -32768 | 32767 | 32767
id:26828 | MODBUS_HOLDING_REGISTER | 5194 | 1 |  | s16 | -32768 | 32767 | 32767
id:26829 | MODBUS_HOLDING_REGISTER | 5195 | 1 |  | s16 | -32768 | 32767 | 32767
id:26830 | MODBUS_HOLDING_REGISTER | 5196 | 1 |  | s16 | -32768 | 32767 | 32767
id:26831 | MODBUS_HOLDING_REGISTER | 5197 | 1 |  | s16 | -32768 | 32767 | 32767
id:26832 | MODBUS_HOLDING_REGISTER | 5198 | 1 |  | s16 | -32768 | 32767 | 32767
id:26833 | MODBUS_HOLDING_REGISTER | 5199 | 1 |  | s16 | -32768 | 32767 | 32767
id:26834 | MODBUS_HOLDING_REGISTER | 5200 | 1 |  | s16 | -32768 | 32767 | 32767
id:26835 | MODBUS_HOLDING_REGISTER | 5201 | 1 |  | s16 | -32768 | 32767 | 32767
id:26836 | MODBUS_HOLDING_REGISTER | 5202 | 1 |  | s16 | -32768 | 32767 | 32767
id:26837 | MODBUS_HOLDING_REGISTER | 5203 | 1 |  | s16 | -32768 | 32767 | 32767
id:26838 | MODBUS_HOLDING_REGISTER | 5204 | 1 |  | s16 | -32768 | 32767 | 32767
id:26839 | MODBUS_HOLDING_REGISTER | 5205 | 1 |  | s16 | -32768 | 32767 | 32767
id:26840 | MODBUS_HOLDING_REGISTER | 5206 | 1 |  | s16 | -32768 | 32767 | 32767
id:26865 | MODBUS_HOLDING_REGISTER | 5181 | 1 |  | u8 | 0 | 1 | 0
id:26867 | MODBUS_HOLDING_REGISTER | 5182 | 1 |  | u8 | 0 | 0 | 0
Heating, compressor only | MODBUS_INPUT_REGISTER | 1585 | 10 | kWh | u32 | 0 | 0 | 0
Hot water, including int. add. heat | MODBUS_INPUT_REGISTER | 1575 | 10 | kWh | u32 | 0 | 0 | 0
id:27790 | MODBUS_INPUT_REGISTER | 2437 | 1 |  | u8 | 0 | 0 | 0
id:27791 | MODBUS_INPUT_REGISTER | 2438 | 1 |  | u8 | 0 | 0 | 0
id:27792 | MODBUS_INPUT_REGISTER | 2439 | 1 |  | u8 | 0 | 0 | 0
id:27793 | MODBUS_INPUT_REGISTER | 2440 | 1 |  | u8 | 0 | 0 | 0
id:27794 | MODBUS_INPUT_REGISTER | 2441 | 1 |  | u8 | 0 | 0 | 0
id:27795 | MODBUS_INPUT_REGISTER | 2442 | 1 |  | u8 | 0 | 0 | 0
id:27796 | MODBUS_INPUT_REGISTER | 2443 | 1 |  | u8 | 0 | 0 | 0
id:27797 | MODBUS_INPUT_REGISTER | 2444 | 1 |  | u8 | 0 | 0 | 0
id:27814 | MODBUS_INPUT_REGISTER | 46 | 10 | A | u32 | 0 | 0 | 0
id:27815 | MODBUS_INPUT_REGISTER | 48 | 10 | A | u32 | 0 | 0 | 0
id:27816 | MODBUS_INPUT_REGISTER | 50 | 10 | A | u32 | 0 | 0 | 0
id:27818 | MODBUS_HOLDING_REGISTER | 5459 | 1 |  | u8 | 0 | 1 | 0
id:27819 | MODBUS_HOLDING_REGISTER | 5460 | 1 |  | u8 | 0 | 1 | 0
id:27854 | MODBUS_HOLDING_REGISTER | 5078 | 1 |  | u8 | 0 | 1 | 0
id:27855 | MODBUS_HOLDING_REGISTER | 5079 | 1 |  | u8 | 0 | 100 | 0
id:28034 | MODBUS_INPUT_REGISTER | 2445 | 10 | °C | s16 | 0 | 0 | 0
id:28035 | MODBUS_INPUT_REGISTER | 2446 | 10 | °C | s16 | 0 | 0 | 0
id:28036 | MODBUS_INPUT_REGISTER | 2447 | 10 | °C | s16 | 0 | 0 | 0
id:28037 | MODBUS_INPUT_REGISTER | 2448 | 10 | °C | s16 | 0 | 0 | 0
id:28038 | MODBUS_INPUT_REGISTER | 2449 | 10 | °C | s16 | 0 | 0 | 0
id:28039 | MODBUS_INPUT_REGISTER | 2450 | 10 | °C | s16 | 0 | 0 | 0
id:28040 | MODBUS_INPUT_REGISTER | 2451 | 10 | °C | s16 | 0 | 0 | 0
id:28041 | MODBUS_INPUT_REGISTER | 2452 | 10 | °C | s16 | 0 | 0 | 0
id:28042 | MODBUS_INPUT_REGISTER | 2453 | 10 | °C | s16 | 0 | 0 | 0
id:28200 | MODBUS_HOLDING_REGISTER | 5518 | 1 |  | u8 | 0 | 0 | 0
id:28201 | MODBUS_HOLDING_REGISTER | 5519 | 1 |  | u8 | 0 | 0 | 0
id:28202 | MODBUS_HOLDING_REGISTER | 5520 | 1 |  | u8 | 0 | 0 | 0
id:28203 | MODBUS_HOLDING_REGISTER | 5521 | 1 |  | u8 | 0 | 0 | 0
id:28204 | MODBUS_HOLDING_REGISTER | 5522 | 1 |  | u8 | 0 | 0 | 0
id:28205 | MODBUS_HOLDING_REGISTER | 5523 | 1 |  | u8 | 0 | 0 | 0
id:28206 | MODBUS_HOLDING_REGISTER | 5524 | 1 |  | u8 | 0 | 0 | 0
id:28207 | MODBUS_HOLDING_REGISTER | 5525 | 1 |  | u8 | 0 | 0 | 0
id:28208 | MODBUS_HOLDING_REGISTER | 5470 | 1 |  | u8 | 0 | 0 | 0
id:28209 | MODBUS_HOLDING_REGISTER | 5471 | 1 |  | u8 | 0 | 0 | 0
id:28210 | MODBUS_HOLDING_REGISTER | 5472 | 1 |  | u8 | 0 | 0 | 0
id:28211 | MODBUS_HOLDING_REGISTER | 5473 | 1 |  | u8 | 0 | 0 | 0
id:28212 | MODBUS_HOLDING_REGISTER | 5474 | 1 |  | u8 | 0 | 0 | 0
id:28213 | MODBUS_HOLDING_REGISTER | 5475 | 1 |  | u8 | 0 | 0 | 0
id:28214 | MODBUS_HOLDING_REGISTER | 5476 | 1 |  | u8 | 0 | 0 | 0
id:28215 | MODBUS_HOLDING_REGISTER | 5477 | 1 |  | u8 | 0 | 0 | 0
id:28216 | MODBUS_HOLDING_REGISTER | 5494 | 1 |  | u8 | 0 | 0 | 0
id:28217 | MODBUS_HOLDING_REGISTER | 5495 | 1 |  | u8 | 0 | 0 | 0
id:28218 | MODBUS_HOLDING_REGISTER | 5496 | 1 |  | u8 | 0 | 0 | 0
id:28219 | MODBUS_HOLDING_REGISTER | 5497 | 1 |  | u8 | 0 | 0 | 0
id:28220 | MODBUS_HOLDING_REGISTER | 5498 | 1 |  | u8 | 0 | 0 | 0
id:28221 | MODBUS_HOLDING_REGISTER | 5499 | 1 |  | u8 | 0 | 0 | 0
id:28222 | MODBUS_HOLDING_REGISTER | 5500 | 1 |  | u8 | 0 | 0 | 0
id:28223 | MODBUS_HOLDING_REGISTER | 5501 | 1 |  | u8 | 0 | 0 | 0
id:28224 | MODBUS_HOLDING_REGISTER | 5526 | 1 | Hz | u8 | 0 | 0 | 0
id:28225 | MODBUS_HOLDING_REGISTER | 5527 | 1 | Hz | u8 | 0 | 0 | 0
id:28226 | MODBUS_HOLDING_REGISTER | 5528 | 1 | Hz | u8 | 0 | 0 | 0
id:28227 | MODBUS_HOLDING_REGISTER | 5529 | 1 | Hz | u8 | 0 | 0 | 0
id:28228 | MODBUS_HOLDING_REGISTER | 5530 | 1 | Hz | u8 | 0 | 0 | 0
id:28229 | MODBUS_HOLDING_REGISTER | 5531 | 1 | Hz | u8 | 0 | 0 | 0
id:28230 | MODBUS_HOLDING_REGISTER | 5532 | 1 | Hz | u8 | 0 | 0 | 0
id:28231 | MODBUS_HOLDING_REGISTER | 5533 | 1 | Hz | u8 | 0 | 0 | 0
id:28232 | MODBUS_HOLDING_REGISTER | 5542 | 1 |  | u8 | 0 | 0 | 0
id:28233 | MODBUS_HOLDING_REGISTER | 5543 | 1 |  | u8 | 0 | 0 | 0
id:28234 | MODBUS_HOLDING_REGISTER | 5544 | 1 |  | u8 | 0 | 0 | 0
id:28235 | MODBUS_HOLDING_REGISTER | 5545 | 1 |  | u8 | 0 | 0 | 0
id:28236 | MODBUS_HOLDING_REGISTER | 5546 | 1 |  | u8 | 0 | 0 | 0
id:28237 | MODBUS_HOLDING_REGISTER | 5547 | 1 |  | u8 | 0 | 0 | 0
id:28238 | MODBUS_HOLDING_REGISTER | 5548 | 1 |  | u8 | 0 | 0 | 0
id:28239 | MODBUS_HOLDING_REGISTER | 5549 | 1 |  | u8 | 0 | 0 | 0
id:28240 | MODBUS_HOLDING_REGISTER | 5534 | 1 |  | u8 | 0 | 0 | 0
id:28241 | MODBUS_HOLDING_REGISTER | 5535 | 1 |  | u8 | 0 | 0 | 0
id:28242 | MODBUS_HOLDING_REGISTER | 5536 | 1 |  | u8 | 0 | 0 | 0
id:28243 | MODBUS_HOLDING_REGISTER | 5537 | 1 |  | u8 | 0 | 0 | 0
id:28244 | MODBUS_HOLDING_REGISTER | 5538 | 1 |  | u8 | 0 | 0 | 0
id:28245 | MODBUS_HOLDING_REGISTER | 5539 | 1 |  | u8 | 0 | 0 | 0
id:28246 | MODBUS_HOLDING_REGISTER | 5540 | 1 |  | u8 | 0 | 0 | 0
id:28247 | MODBUS_HOLDING_REGISTER | 5541 | 1 |  | u8 | 0 | 0 | 0
id:28248 | MODBUS_HOLDING_REGISTER | 5478 | 1 | % | u8 | 0 | 0 | 0
id:28249 | MODBUS_HOLDING_REGISTER | 5479 | 1 | % | u8 | 0 | 0 | 0
id:28250 | MODBUS_HOLDING_REGISTER | 5480 | 1 | % | u8 | 0 | 0 | 0
id:28251 | MODBUS_HOLDING_REGISTER | 5481 | 1 | % | u8 | 0 | 0 | 0
id:28252 | MODBUS_HOLDING_REGISTER | 5482 | 1 | % | u8 | 0 | 0 | 0
id:28253 | MODBUS_HOLDING_REGISTER | 5483 | 1 | % | u8 | 0 | 0 | 0
id:28254 | MODBUS_HOLDING_REGISTER | 5484 | 1 | % | u8 | 0 | 0 | 0
id:28255 | MODBUS_HOLDING_REGISTER | 5485 | 1 | % | u8 | 0 | 0 | 0
id:28256 | MODBUS_HOLDING_REGISTER | 5486 | 1 | % | u8 | 0 | 0 | 0
id:28257 | MODBUS_HOLDING_REGISTER | 5487 | 1 | % | u8 | 0 | 0 | 0
id:28258 | MODBUS_HOLDING_REGISTER | 5488 | 1 | % | u8 | 0 | 0 | 0
id:28259 | MODBUS_HOLDING_REGISTER | 5489 | 1 | % | u8 | 0 | 0 | 0
id:28260 | MODBUS_HOLDING_REGISTER | 5490 | 1 | % | u8 | 0 | 0 | 0
id:28261 | MODBUS_HOLDING_REGISTER | 5491 | 1 | % | u8 | 0 | 0 | 0
id:28262 | MODBUS_HOLDING_REGISTER | 5492 | 1 | % | u8 | 0 | 0 | 0
id:28263 | MODBUS_HOLDING_REGISTER | 5493 | 1 | % | u8 | 0 | 0 | 0
id:28264 | MODBUS_HOLDING_REGISTER | 5502 | 1 | % | u8 | 0 | 0 | 0
id:28265 | MODBUS_HOLDING_REGISTER | 5503 | 1 | % | u8 | 0 | 0 | 0
id:28266 | MODBUS_HOLDING_REGISTER | 5504 | 1 | % | u8 | 0 | 0 | 0
id:28267 | MODBUS_HOLDING_REGISTER | 5505 | 1 | % | u8 | 0 | 0 | 0
id:28268 | MODBUS_HOLDING_REGISTER | 5506 | 1 | % | u8 | 0 | 0 | 0
id:28269 | MODBUS_HOLDING_REGISTER | 5507 | 1 | % | u8 | 0 | 0 | 0
id:28270 | MODBUS_HOLDING_REGISTER | 5508 | 1 | % | u8 | 0 | 0 | 0
id:28271 | MODBUS_HOLDING_REGISTER | 5509 | 1 | % | u8 | 0 | 0 | 0
id:28272 | MODBUS_HOLDING_REGISTER | 5510 | 1 | % | u8 | 0 | 0 | 0
id:28273 | MODBUS_HOLDING_REGISTER | 5511 | 1 | % | u8 | 0 | 0 | 0
id:28274 | MODBUS_HOLDING_REGISTER | 5512 | 1 | % | u8 | 0 | 0 | 0
id:28275 | MODBUS_HOLDING_REGISTER | 5513 | 1 | % | u8 | 0 | 0 | 0
id:28276 | MODBUS_HOLDING_REGISTER | 5514 | 1 | % | u8 | 0 | 0 | 0
id:28277 | MODBUS_HOLDING_REGISTER | 5515 | 1 | % | u8 | 0 | 0 | 0
id:28278 | MODBUS_HOLDING_REGISTER | 5516 | 1 | % | u8 | 0 | 0 | 0
id:28279 | MODBUS_HOLDING_REGISTER | 5517 | 1 | % | u8 | 0 | 0 | 0
Boiler temperature (BT52) | MODBUS_INPUT_REGISTER | 3800 | 10 | °C | s16 | 0 | 0 | 0
id:28403 | MODBUS_HOLDING_REGISTER | 5600 | 1 |  | s32 | -10000 | 10000 | 100
id:28404 | MODBUS_HOLDING_REGISTER | 5602 | 1 |  | s32 | -10000 | 10000 | 100
id:28405 | MODBUS_HOLDING_REGISTER | 5604 | 1 |  | s32 | -10000 | 10000 | 100
id:28406 | MODBUS_HOLDING_REGISTER | 5606 | 1 |  | s32 | -10000 | 10000 | 100
id:28407 | MODBUS_HOLDING_REGISTER | 5608 | 1 |  | s32 | -10000 | 10000 | 100
id:28408 | MODBUS_HOLDING_REGISTER | 5610 | 1 |  | s32 | -10000 | 10000 | 100
id:28409 | MODBUS_HOLDING_REGISTER | 5612 | 1 |  | s32 | -10000 | 10000 | 100
id:28410 | MODBUS_HOLDING_REGISTER | 5614 | 1 |  | s32 | -10000 | 10000 | 100
id:28411 | MODBUS_HOLDING_REGISTER | 5616 | 1 |  | s32 | -10000 | 10000 | 100
id:28412 | MODBUS_HOLDING_REGISTER | 5618 | 1 |  | s32 | -10000 | 10000 | 100
id:28413 | MODBUS_HOLDING_REGISTER | 5620 | 1 |  | s32 | -10000 | 10000 | 100
id:28414 | MODBUS_HOLDING_REGISTER | 5622 | 1 |  | s32 | -10000 | 10000 | 100
id:28415 | MODBUS_HOLDING_REGISTER | 5624 | 1 |  | s32 | -10000 | 10000 | 100
id:28416 | MODBUS_HOLDING_REGISTER | 5626 | 1 |  | s32 | -10000 | 10000 | 100
id:28417 | MODBUS_HOLDING_REGISTER | 5628 | 1 |  | s32 | -10000 | 10000 | 100
id:28418 | MODBUS_HOLDING_REGISTER | 5630 | 1 |  | s32 | -10000 | 10000 | 100
id:28419 | MODBUS_HOLDING_REGISTER | 5632 | 1 |  | s32 | -10000 | 10000 | 100
id:28420 | MODBUS_HOLDING_REGISTER | 5634 | 1 |  | s32 | -10000 | 10000 | 100
id:28421 | MODBUS_HOLDING_REGISTER | 5636 | 1 |  | s32 | -10000 | 10000 | 100
id:28422 | MODBUS_HOLDING_REGISTER | 5638 | 1 |  | s32 | -10000 | 10000 | 100
id:28423 | MODBUS_HOLDING_REGISTER | 5640 | 1 |  | s32 | -10000 | 10000 | 100
id:28424 | MODBUS_HOLDING_REGISTER | 5642 | 1 |  | s32 | -10000 | 10000 | 100
id:28425 | MODBUS_HOLDING_REGISTER | 5644 | 1 |  | s32 | -10000 | 10000 | 100
id:28426 | MODBUS_HOLDING_REGISTER | 5646 | 1 |  | s32 | -10000 | 10000 | 100
id:28427 | MODBUS_HOLDING_REGISTER | 5648 | 1 |  | s32 | -10000 | 10000 | 100
id:28428 | MODBUS_HOLDING_REGISTER | 5650 | 1 |  | s32 | -10000 | 10000 | 100
id:28429 | MODBUS_HOLDING_REGISTER | 5652 | 1 |  | s32 | -10000 | 10000 | 100
id:28430 | MODBUS_HOLDING_REGISTER | 5654 | 1 |  | s32 | -10000 | 10000 | 100
id:28431 | MODBUS_HOLDING_REGISTER | 5656 | 1 |  | s32 | -10000 | 10000 | 100
id:28432 | MODBUS_HOLDING_REGISTER | 5658 | 1 |  | s32 | -10000 | 10000 | 100
id:28433 | MODBUS_HOLDING_REGISTER | 5660 | 1 |  | s32 | -10000 | 10000 | 100
id:28434 | MODBUS_HOLDING_REGISTER | 5662 | 1 |  | s32 | -10000 | 10000 | 100
id:28435 | MODBUS_HOLDING_REGISTER | 5664 | 1 |  | s32 | -10000 | 10000 | 100
id:28436 | MODBUS_HOLDING_REGISTER | 5666 | 1 |  | s32 | -10000 | 10000 | 100
id:28437 | MODBUS_HOLDING_REGISTER | 5668 | 1 |  | s32 | -10000 | 10000 | 100
id:28438 | MODBUS_HOLDING_REGISTER | 5670 | 1 |  | s32 | -10000 | 10000 | 100
id:28439 | MODBUS_HOLDING_REGISTER | 5672 | 1 |  | s32 | -10000 | 10000 | 100
id:28440 | MODBUS_HOLDING_REGISTER | 5674 | 1 |  | s32 | -10000 | 10000 | 100
id:28441 | MODBUS_HOLDING_REGISTER | 5676 | 1 |  | s32 | -10000 | 10000 | 100
id:28442 | MODBUS_HOLDING_REGISTER | 5678 | 1 |  | s32 | -10000 | 10000 | 100
id:28443 | MODBUS_HOLDING_REGISTER | 5680 | 1 |  | s32 | -10000 | 10000 | 100
id:28444 | MODBUS_HOLDING_REGISTER | 5682 | 1 |  | s32 | -10000 | 10000 | 100
id:28445 | MODBUS_HOLDING_REGISTER | 5684 | 1 |  | s32 | -10000 | 10000 | 100
id:28446 | MODBUS_HOLDING_REGISTER | 5686 | 1 |  | s32 | -10000 | 10000 | 100
id:28447 | MODBUS_HOLDING_REGISTER | 5688 | 1 |  | s32 | -10000 | 10000 | 100
id:28448 | MODBUS_HOLDING_REGISTER | 5690 | 1 |  | s32 | -10000 | 10000 | 100
id:28449 | MODBUS_HOLDING_REGISTER | 5692 | 1 |  | s32 | -10000 | 10000 | 100
id:28450 | MODBUS_HOLDING_REGISTER | 5694 | 1 |  | s32 | -10000 | 10000 | 100
id:28451 | MODBUS_HOLDING_REGISTER | 5696 | 1 |  | s32 | -10000 | 10000 | 100
id:28452 | MODBUS_HOLDING_REGISTER | 5698 | 1 |  | s32 | -10000 | 10000 | 100
id:28453 | MODBUS_HOLDING_REGISTER | 5700 | 1 |  | s32 | -10000 | 10000 | 100
id:28454 | MODBUS_HOLDING_REGISTER | 5702 | 1 |  | s32 | -10000 | 10000 | 100
id:28455 | MODBUS_HOLDING_REGISTER | 5704 | 1 |  | s32 | -10000 | 10000 | 100
id:28456 | MODBUS_HOLDING_REGISTER | 5706 | 1 |  | s32 | -10000 | 10000 | 100
id:28457 | MODBUS_HOLDING_REGISTER | 5708 | 1 |  | s32 | -10000 | 10000 | 100
id:28458 | MODBUS_HOLDING_REGISTER | 5710 | 1 |  | s32 | -10000 | 10000 | 100
id:28459 | MODBUS_HOLDING_REGISTER | 5712 | 1 |  | s32 | -10000 | 10000 | 100
id:28460 | MODBUS_HOLDING_REGISTER | 5714 | 1 |  | s32 | -10000 | 10000 | 100
id:28461 | MODBUS_HOLDING_REGISTER | 5716 | 1 |  | s32 | -10000 | 10000 | 100
id:28462 | MODBUS_HOLDING_REGISTER | 5718 | 1 |  | s32 | -10000 | 10000 | 100
id:28463 | MODBUS_HOLDING_REGISTER | 5720 | 1 |  | s32 | -10000 | 10000 | 100
id:28464 | MODBUS_HOLDING_REGISTER | 5722 | 1 |  | s32 | -10000 | 10000 | 100
id:28465 | MODBUS_HOLDING_REGISTER | 5724 | 1 |  | s32 | -10000 | 10000 | 100
id:28466 | MODBUS_HOLDING_REGISTER | 5726 | 1 |  | s32 | -10000 | 10000 | 100
id:28467 | MODBUS_HOLDING_REGISTER | 5728 | 1 |  | s32 | -10000 | 10000 | 100
id:28468 | MODBUS_HOLDING_REGISTER | 5730 | 1 |  | s32 | -10000 | 10000 | 100
id:28469 | MODBUS_HOLDING_REGISTER | 5732 | 1 |  | s32 | -10000 | 10000 | 100
id:28470 | MODBUS_HOLDING_REGISTER | 5734 | 1 |  | s32 | -10000 | 10000 | 100
id:28471 | MODBUS_HOLDING_REGISTER | 5736 | 1 |  | s32 | -10000 | 10000 | 100
id:28472 | MODBUS_HOLDING_REGISTER | 5738 | 1 |  | s32 | -10000 | 10000 | 100
id:28473 | MODBUS_HOLDING_REGISTER | 5740 | 1 |  | s32 | -10000 | 10000 | 100
id:28474 | MODBUS_HOLDING_REGISTER | 5742 | 1 |  | s32 | -10000 | 10000 | 100
id:28475 | MODBUS_HOLDING_REGISTER | 5744 | 1 |  | s32 | -10000 | 10000 | 100
id:28476 | MODBUS_HOLDING_REGISTER | 5746 | 1 |  | s32 | -10000 | 10000 | 100
id:28477 | MODBUS_HOLDING_REGISTER | 5748 | 1 |  | s32 | -10000 | 10000 | 100
id:28478 | MODBUS_HOLDING_REGISTER | 5750 | 1 |  | s32 | -10000 | 10000 | 100
id:28479 | MODBUS_HOLDING_REGISTER | 5752 | 1 |  | s32 | -10000 | 10000 | 100
id:28480 | MODBUS_HOLDING_REGISTER | 5754 | 1 |  | s32 | -10000 | 10000 | 100
id:28481 | MODBUS_HOLDING_REGISTER | 5756 | 1 |  | s32 | -10000 | 10000 | 100
id:28482 | MODBUS_HOLDING_REGISTER | 5758 | 1 |  | s32 | -10000 | 10000 | 100
id:28483 | MODBUS_HOLDING_REGISTER | 5760 | 1 |  | s32 | -10000 | 10000 | 100
id:28484 | MODBUS_HOLDING_REGISTER | 5762 | 1 |  | s32 | -10000 | 10000 | 100
id:28485 | MODBUS_HOLDING_REGISTER | 5764 | 1 |  | s32 | -10000 | 10000 | 100
id:28486 | MODBUS_HOLDING_REGISTER | 5766 | 1 |  | s32 | -10000 | 10000 | 100
id:28487 | MODBUS_HOLDING_REGISTER | 5768 | 1 |  | s32 | -10000 | 10000 | 100
id:28488 | MODBUS_HOLDING_REGISTER | 5770 | 1 |  | s32 | -10000 | 10000 | 100
id:28489 | MODBUS_HOLDING_REGISTER | 5772 | 1 |  | s32 | -10000 | 10000 | 100
id:28490 | MODBUS_HOLDING_REGISTER | 5774 | 1 |  | s32 | -10000 | 10000 | 100
id:28491 | MODBUS_HOLDING_REGISTER | 5776 | 1 |  | s32 | -10000 | 10000 | 100
id:28492 | MODBUS_HOLDING_REGISTER | 5778 | 1 |  | s32 | -10000 | 10000 | 100
id:28493 | MODBUS_HOLDING_REGISTER | 5780 | 1 |  | s32 | -10000 | 10000 | 100
id:28494 | MODBUS_HOLDING_REGISTER | 5782 | 1 |  | s32 | -10000 | 10000 | 100
id:28495 | MODBUS_HOLDING_REGISTER | 5784 | 1 |  | s32 | -10000 | 10000 | 100
id:28496 | MODBUS_HOLDING_REGISTER | 5786 | 1 |  | s32 | -10000 | 10000 | 100
id:28497 | MODBUS_HOLDING_REGISTER | 5788 | 1 |  | s32 | -10000 | 10000 | 100
id:28498 | MODBUS_HOLDING_REGISTER | 5790 | 1 |  | s32 | -10000 | 10000 | 100
id:28500 | MODBUS_HOLDING_REGISTER | 5792 | 1 |  | s32 | -10000 | 10000 | 100
id:28501 | MODBUS_HOLDING_REGISTER | 5794 | 1 |  | s32 | -10000 | 10000 | 100
id:28502 | MODBUS_HOLDING_REGISTER | 5796 | 1 |  | s32 | -10000 | 10000 | 100
id:28503 | MODBUS_HOLDING_REGISTER | 5798 | 1 |  | s32 | -10000 | 10000 | 100
id:28504 | MODBUS_HOLDING_REGISTER | 5800 | 1 |  | s32 | -10000 | 10000 | 100
id:28505 | MODBUS_HOLDING_REGISTER | 5802 | 1 |  | s32 | -10000 | 10000 | 100
id:28506 | MODBUS_HOLDING_REGISTER | 5804 | 1 |  | s32 | -10000 | 10000 | 100
id:28507 | MODBUS_HOLDING_REGISTER | 5806 | 1 |  | s32 | -10000 | 10000 | 100
id:28508 | MODBUS_HOLDING_REGISTER | 5808 | 1 |  | s32 | -10000 | 10000 | 100
id:28509 | MODBUS_HOLDING_REGISTER | 5810 | 1 |  | s32 | -10000 | 10000 | 100
id:28510 | MODBUS_HOLDING_REGISTER | 5812 | 1 |  | s32 | -10000 | 10000 | 100
id:28511 | MODBUS_HOLDING_REGISTER | 5814 | 1 |  | s32 | -10000 | 10000 | 100
id:28512 | MODBUS_HOLDING_REGISTER | 5816 | 1 |  | s32 | -10000 | 10000 | 100
id:28513 | MODBUS_HOLDING_REGISTER | 5818 | 1 |  | s32 | -10000 | 10000 | 100
id:28514 | MODBUS_HOLDING_REGISTER | 5820 | 1 |  | s32 | -10000 | 10000 | 100
id:28515 | MODBUS_HOLDING_REGISTER | 5822 | 1 |  | s32 | -10000 | 10000 | 100
id:28516 | MODBUS_HOLDING_REGISTER | 5824 | 1 |  | s32 | -10000 | 10000 | 100
id:28517 | MODBUS_HOLDING_REGISTER | 5826 | 1 |  | s32 | -10000 | 10000 | 100
id:28518 | MODBUS_HOLDING_REGISTER | 5828 | 1 |  | s32 | -10000 | 10000 | 100
id:28519 | MODBUS_HOLDING_REGISTER | 5830 | 1 |  | s32 | -10000 | 10000 | 100
id:28520 | MODBUS_HOLDING_REGISTER | 5832 | 1 |  | s32 | -10000 | 10000 | 100
id:28521 | MODBUS_HOLDING_REGISTER | 5834 | 1 |  | s32 | -10000 | 10000 | 100
id:28522 | MODBUS_HOLDING_REGISTER | 5836 | 1 |  | s32 | -10000 | 10000 | 100
id:28523 | MODBUS_HOLDING_REGISTER | 5838 | 1 |  | s32 | -10000 | 10000 | 100
id:28524 | MODBUS_HOLDING_REGISTER | 5840 | 1 |  | s32 | -10000 | 10000 | 100
id:28525 | MODBUS_HOLDING_REGISTER | 5842 | 1 |  | s32 | -10000 | 10000 | 100
id:28526 | MODBUS_HOLDING_REGISTER | 5844 | 1 |  | s32 | -10000 | 10000 | 100
id:28527 | MODBUS_HOLDING_REGISTER | 5846 | 1 |  | s32 | -10000 | 10000 | 100
id:28528 | MODBUS_HOLDING_REGISTER | 5848 | 1 |  | s32 | -10000 | 10000 | 100
id:28529 | MODBUS_HOLDING_REGISTER | 5850 | 1 |  | s32 | -10000 | 10000 | 100
id:28530 | MODBUS_HOLDING_REGISTER | 5852 | 1 |  | s32 | -10000 | 10000 | 100
id:28531 | MODBUS_HOLDING_REGISTER | 5854 | 1 |  | s32 | -10000 | 10000 | 100
id:28532 | MODBUS_HOLDING_REGISTER | 5856 | 1 |  | s32 | -10000 | 10000 | 100
id:28533 | MODBUS_HOLDING_REGISTER | 5858 | 1 |  | s32 | -10000 | 10000 | 100
id:28534 | MODBUS_HOLDING_REGISTER | 5860 | 1 |  | s32 | -10000 | 10000 | 100
id:28535 | MODBUS_HOLDING_REGISTER | 5862 | 1 |  | s32 | -10000 | 10000 | 100
id:28536 | MODBUS_HOLDING_REGISTER | 5864 | 1 |  | s32 | -10000 | 10000 | 100
id:28537 | MODBUS_HOLDING_REGISTER | 5866 | 1 |  | s32 | -10000 | 10000 | 100
id:28538 | MODBUS_HOLDING_REGISTER | 5868 | 1 |  | s32 | -10000 | 10000 | 100
id:28539 | MODBUS_HOLDING_REGISTER | 5870 | 1 |  | s32 | -10000 | 10000 | 100
id:28540 | MODBUS_HOLDING_REGISTER | 5872 | 1 |  | s32 | -10000 | 10000 | 100
id:28541 | MODBUS_HOLDING_REGISTER | 5874 | 1 |  | s32 | -10000 | 10000 | 100
id:28542 | MODBUS_HOLDING_REGISTER | 5876 | 1 |  | s32 | -10000 | 10000 | 100
id:28543 | MODBUS_HOLDING_REGISTER | 5878 | 1 |  | s32 | -10000 | 10000 | 100
id:28544 | MODBUS_HOLDING_REGISTER | 5880 | 1 |  | s32 | -10000 | 10000 | 100
id:28545 | MODBUS_HOLDING_REGISTER | 5882 | 1 |  | s32 | -10000 | 10000 | 100
id:28546 | MODBUS_HOLDING_REGISTER | 5884 | 1 |  | s32 | -10000 | 10000 | 100
id:28547 | MODBUS_HOLDING_REGISTER | 5886 | 1 |  | s32 | -10000 | 10000 | 100
id:28548 | MODBUS_HOLDING_REGISTER | 5888 | 1 |  | s32 | -10000 | 10000 | 100
id:28549 | MODBUS_HOLDING_REGISTER | 5890 | 1 |  | s32 | -10000 | 10000 | 100
id:28550 | MODBUS_HOLDING_REGISTER | 5892 | 1 |  | s32 | -10000 | 10000 | 100
id:28551 | MODBUS_HOLDING_REGISTER | 5894 | 1 |  | s32 | -10000 | 10000 | 100
id:28552 | MODBUS_HOLDING_REGISTER | 5896 | 1 |  | s32 | -10000 | 10000 | 100
id:28553 | MODBUS_HOLDING_REGISTER | 5898 | 1 |  | s32 | -10000 | 10000 | 100
id:28554 | MODBUS_HOLDING_REGISTER | 5900 | 1 |  | s32 | -10000 | 10000 | 100
id:28555 | MODBUS_HOLDING_REGISTER | 5902 | 1 |  | s32 | -10000 | 10000 | 100
id:28556 | MODBUS_HOLDING_REGISTER | 5904 | 1 |  | s32 | -10000 | 10000 | 100
id:28557 | MODBUS_HOLDING_REGISTER | 5906 | 1 |  | s32 | -10000 | 10000 | 100
id:28558 | MODBUS_HOLDING_REGISTER | 5908 | 1 |  | s32 | -10000 | 10000 | 100
id:28559 | MODBUS_HOLDING_REGISTER | 5910 | 1 |  | s32 | -10000 | 10000 | 100
id:28560 | MODBUS_HOLDING_REGISTER | 5912 | 1 |  | s32 | -10000 | 10000 | 100
id:28561 | MODBUS_HOLDING_REGISTER | 5914 | 1 |  | s32 | -10000 | 10000 | 100
id:28562 | MODBUS_HOLDING_REGISTER | 5916 | 1 |  | s32 | -10000 | 10000 | 100
id:28563 | MODBUS_HOLDING_REGISTER | 5918 | 1 |  | s32 | -10000 | 10000 | 100
id:28564 | MODBUS_HOLDING_REGISTER | 5920 | 1 |  | s32 | -10000 | 10000 | 100
id:28565 | MODBUS_HOLDING_REGISTER | 5922 | 1 |  | s32 | -10000 | 10000 | 100
id:28566 | MODBUS_HOLDING_REGISTER | 5924 | 1 |  | s32 | -10000 | 10000 | 100
id:28567 | MODBUS_HOLDING_REGISTER | 5926 | 1 |  | s32 | -10000 | 10000 | 100
id:28568 | MODBUS_HOLDING_REGISTER | 5928 | 1 |  | s32 | -10000 | 10000 | 100
id:28569 | MODBUS_HOLDING_REGISTER | 5930 | 1 |  | s32 | -10000 | 10000 | 100
id:28570 | MODBUS_HOLDING_REGISTER | 5932 | 1 |  | s32 | -10000 | 10000 | 100
id:28571 | MODBUS_HOLDING_REGISTER | 5934 | 1 |  | s32 | -10000 | 10000 | 100
id:28572 | MODBUS_HOLDING_REGISTER | 5936 | 1 |  | s32 | -10000 | 10000 | 100
id:28573 | MODBUS_HOLDING_REGISTER | 5938 | 1 |  | s32 | -10000 | 10000 | 100
id:28574 | MODBUS_HOLDING_REGISTER | 5940 | 1 |  | s32 | -10000 | 10000 | 100
id:28575 | MODBUS_HOLDING_REGISTER | 5942 | 1 |  | s32 | -10000 | 10000 | 100
id:28576 | MODBUS_HOLDING_REGISTER | 5944 | 1 |  | s32 | -10000 | 10000 | 100
id:28577 | MODBUS_HOLDING_REGISTER | 5946 | 1 |  | s32 | -10000 | 10000 | 100
id:28578 | MODBUS_HOLDING_REGISTER | 5948 | 1 |  | s32 | -10000 | 10000 | 100
id:28579 | MODBUS_HOLDING_REGISTER | 5950 | 1 |  | s32 | -10000 | 10000 | 100
id:28580 | MODBUS_HOLDING_REGISTER | 5952 | 1 |  | s32 | -10000 | 10000 | 100
id:28581 | MODBUS_HOLDING_REGISTER | 5954 | 1 |  | s32 | -10000 | 10000 | 100
id:28582 | MODBUS_HOLDING_REGISTER | 5956 | 1 |  | s32 | -10000 | 10000 | 100
id:28583 | MODBUS_HOLDING_REGISTER | 5958 | 1 |  | s32 | -10000 | 10000 | 100
id:28584 | MODBUS_HOLDING_REGISTER | 5960 | 1 |  | s32 | -10000 | 10000 | 100
id:28585 | MODBUS_HOLDING_REGISTER | 5962 | 1 |  | s32 | -10000 | 10000 | 100
id:28586 | MODBUS_HOLDING_REGISTER | 5964 | 1 |  | s32 | -10000 | 10000 | 100
id:28587 | MODBUS_HOLDING_REGISTER | 5966 | 1 |  | s32 | -10000 | 10000 | 100
id:28588 | MODBUS_HOLDING_REGISTER | 5968 | 1 |  | s32 | -10000 | 10000 | 100
id:28589 | MODBUS_HOLDING_REGISTER | 5970 | 1 |  | s32 | -10000 | 10000 | 100
id:28590 | MODBUS_HOLDING_REGISTER | 5972 | 1 |  | s32 | -10000 | 10000 | 100
id:28591 | MODBUS_HOLDING_REGISTER | 5974 | 1 |  | s32 | -10000 | 10000 | 100
id:28592 | MODBUS_HOLDING_REGISTER | 5976 | 1 |  | s32 | -10000 | 10000 | 100
id:28593 | MODBUS_HOLDING_REGISTER | 5978 | 1 |  | s32 | -10000 | 10000 | 100
id:28594 | MODBUS_HOLDING_REGISTER | 5980 | 1 |  | s32 | -10000 | 10000 | 100
id:28595 | MODBUS_HOLDING_REGISTER | 5982 | 1 |  | s32 | -10000 | 10000 | 100
id:29258 | MODBUS_HOLDING_REGISTER | 5984 | 1 | kW | u16 | 0 | 65535 | 0
Current power | MODBUS_INPUT_REGISTER | 2727 | 100 | kW | u32 | 0 | 0 | 0
id:29292 | MODBUS_HOLDING_REGISTER | 5985 | 1 |  | s16 | 0 | 20 | 0
id:29970 | MODBUS_HOLDING_REGISTER | 5986 | 1 |  | u8 | 0 | 1 | 0
id:29971 | MODBUS_HOLDING_REGISTER | 5987 | 10 | °C | s16 | 0 | 0 | 0
Input AUX7 | MODBUS_HOLDING_REGISTER | 1555 | 1 |  | u8 | 0 | 68 | 0
Input AUX8 | MODBUS_HOLDING_REGISTER | 1556 | 1 |  | u8 | 0 | 68 | 0
Input AUX9 | MODBUS_HOLDING_REGISTER | 1557 | 1 |  | u8 | 0 | 68 | 0
id:55076 | MODBUS_HOLDING_REGISTER | 2877 | 1 |  | u8 | 0 | 1 | 0
id:55077 | MODBUS_HOLDING_REGISTER | 2878 | 1 |  | u8 | 0 | 1 | 0
id:55078 | MODBUS_HOLDING_REGISTER | 2879 | 1 |  | u8 | 0 | 1 | 0
id:55079 | MODBUS_HOLDING_REGISTER | 2880 | 1 |  | u8 | 0 | 1 | 0
id:55080 | MODBUS_HOLDING_REGISTER | 2881 | 1 |  | u8 | 0 | 1 | 0
id:55081 | MODBUS_HOLDING_REGISTER | 2882 | 1 |  | u8 | 0 | 1 | 0
id:55082 | MODBUS_HOLDING_REGISTER | 2883 | 1 |  | u8 | 0 | 1 | 0
id:55083 | MODBUS_HOLDING_REGISTER | 2884 | 1 |  | u8 | 0 | 1 | 0
Immersion heater power, emergency mode | MODBUS_HOLDING_REGISTER | 3028 | 100 | kW | s16 | 0 | 4500 | 940
Disable emergency restart GP1 | MODBUS_HOLDING_REGISTER | 3986 | 1 |  | u8 | 0 | 1 | 0
EEV Control Mode (EB101) | MODBUS_INPUT_REGISTER | 2413 | 1 |  | u8 | 0 | 0 | 0
EEV State (EB101) | MODBUS_INPUT_REGISTER | 2421 | 1 |  | u8 | 0 | 0 | 0
id:55495 | MODBUS_HOLDING_REGISTER | 5550 | 1 |  | u8 | 0 | 1 | 0
id:55496 | MODBUS_HOLDING_REGISTER | 5207 | 10 | °C | s16 | 0 | 0 | 0
id:55749 | MODBUS_HOLDING_REGISTER | 5551 | 1 |  | u8 | 0 | 1 | 0

## modbus_addresses_common
Title Register type Register Division factor Unit Size of variable Min value Max value Default value
Current outdoor temperature (BT1) MODBUS_INPUT_REGISTER 1 10 Â°C s16 0 0 0
Average temperature (BT1) MODBUS_INPUT_REGISTER 37 10 Â°C s16 0 0 0
External supply line (BT25) MODBUS_INPUT_REGISTER 39 10 Â°C s16 0 0 0
- MODBUS_INPUT_REGISTER 60 10 Â°C s16 0 0 0
- MODBUS_INPUT_REGISTER 61 10 Â°C s16 0 0 0
- MODBUS_INPUT_REGISTER 62 10 Â°C s16 0 0 0
- MODBUS_INPUT_REGISTER 63 10 Â°C s16 0 0 0
- MODBUS_INPUT_REGISTER 64 10 Â°C s16 0 0 0
- MODBUS_INPUT_REGISTER 65 10 Â°C s16 0 0 0
Return line (BT71) MODBUS_INPUT_REGISTER 88 10 Â°C s16 0 0 0
Degree minutes MODBUS_HOLDING_REGISTER 11 10 DM s32 -30000 30000 0
Injection (EB101-BT81) MODBUS_INPUT_REGISTER 552 10 Â°C s16 0 0 0
Evaporator (EB101-BT84) MODBUS_INPUT_REGISTER 555 10 Â°C s16 0 0 0
Calculated supply climate system 1 MODBUS_INPUT_REGISTER 1017 10 Â°C s16 0 0 0
Operating mode internal add. heat MODBUS_INPUT_REGISTER 1029 1 u8 0 0 0
External heating medium pump (GP10) status MODBUS_INPUT_REGISTER 1066 1 u8 0 0 0
Return line (EB101-BT3) MODBUS_INPUT_REGISTER 1475 10 Â°C s16 0 0 0
Condenser sensor | supply line (EB101-BT12) MODBUS_INPUT_REGISTER 1478 10 Â°C s16 0 0 0
Discharge (EB101-BT14) MODBUS_INPUT_REGISTER 1479 10 Â°C s16 0 0 0
Liquid line (EB101-BT15) MODBUS_INPUT_REGISTER 1480 10 Â°C s16 0 0 0
Suction gas (EB101-BT17) MODBUS_INPUT_REGISTER 1481 10 Â°C s16 0 0 0
Outdoor temperature (EB101-BT28) MODBUS_INPUT_REGISTER 1621 10 Â°C s16 0 0 0
Evaporator (EB101-BT16) MODBUS_INPUT_REGISTER 1622 10 Â°C s16 0 0 0
Charge pump speed (EB101-GP12) MODBUS_INPUT_REGISTER 1636 1 % u8 0 0 0
Low pressure (EB101-BP8) MODBUS_INPUT_REGISTER 1802 10 bar s16 0 0 0
Current compressor frequency (EB101) MODBUS_INPUT_REGISTER 1803 10 Hz s16 0 0 0
Protection mode (EB101) MODBUS_INPUT_REGISTER 1804 1 u16 0 0 0
Requested compressor frequency (EB101) MODBUS_INPUT_REGISTER 1854 1 Hz u8 0 0 0
Evaporator 2 (EB101-EP14-BT16) MODBUS_INPUT_REGISTER 1966 10 Â°C s16 0 0 0
Alarm number MODBUS_INPUT_REGISTER 1975 1 s16 0 0 0
id:27814 MODBUS_INPUT_REGISTER 46 10 A u32 0 0 0
id:27815 MODBUS_INPUT_REGISTER 48 10 A u32 0 0 0
id:27816 MODBUS_INPUT_REGISTER 50 10 A u32 0 0 0